## EU - Qualifying (>=20MW)
Terminal | Terminal ID | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | Turbine/Genset Class | References
Adriatic LNG Terminal | T100000130466 | 3x GE10 turbines (aeroderivative, electric generation) | ~10 MW each | 30 MW total | Aggregate >=20 MW (aeroderivative rule) | Aeroderivative gas turbine (GE10) | https://www.ge.com/news/press-releases/ge-oil-gas-powers-worlds-first-offshore-gravity-based-lng-terminal https://www.adriaticlng.it/wps/wcm/connect/web2/site/en/The+Terminal/Technical+features/
Brunsbuttel LNG Terminal | T100000130460 | 4x Wartsila 50DF engines (3x8L50DF + 1x6L50DF) | ~9.7 MW / ~7.3 MW | ~36.4 MW total (estimated) | Aggregate >=20 MW (genset rule) | Reciprocating dual-fuel genset | https://energy-terminal.de/fileadmin/user_upload/Test/Meldungen/2024-02-09_Para8a-Bescheid.pdf https://www.wartsila.com/energy/engine-power-plant-solutions/engine-power-plant-products/wartsila-50df-dual-fuel-engine
Gioia Tauro LNG Terminal | T100000130472 | 1x gas turbine electric generator | 20 MW | 20 MW | Individual = 20 MW (meets threshold) | Gas turbine | https://va.mite.gov.it/File/Documento/2773
Hammerfest LNG Snohvit Terminal | T100000130494 | 5x GE LM6000PD (electric generation) | ~45.8 MW each (229/5) | 229 MW total | Qualifies both ways (individual AND aggregate) | Aeroderivative gas turbine | https://snl.no/Melk%C3%B8ya https://www.equinor.com/news/20221220-high-gas-exports-and-emissions-cuts-from-hammerfest-lng https://www.equinor.com/news/20230808-governmental-green-light-snohvit-future
Le Havre FSRU | T100000131008 | 4x dual-fuel engines/gensets | 3x11.4 MW + 1x5.7 MW | 39.9 MW total | Aggregate >=20 MW (genset rule) | Reciprocating dual-fuel genset | https://www.seine-maritime.gouv.fr/index.php/contenu/telechargement/57970/407572/file/Arr%C3%AAt%C3%A9%20pr%C3%A9fectoral%2009.08.23%20TOTALENERGIES%20LNG%20Services%20France%20-%20Le%20Havre.pdf https://www.aukevisser.nl/supertankers/gas-2/id737.htm
Mukran LNG Terminal (Deutsche Ostsee) | T100000131141 | Dual-fuel engines aboard 2 FSRUs (Neptune + Energos Power) | not broken out individually | 39.9 MW total | Aggregate >=20 MW (genset rule) | Reciprocating dual-fuel genset | https://www.stalu-mv.de/vp/Service/Presse_Bekanntmachungen/?id=200530&processor=processor.sa.pressemitteilung https://www.stalu-mv.de/vp/Service/Bekanntmachungen-nach-BImSchG/Bereich-Immissionsschutz/?processor=processor.sa.bimschbekannt&bekann_id=1719 https://www.energie-und-management.de/nachrichten/recht/detail/deutsche-regas-darf-mukran-dauerhaft-ohne-landstrom-betreiben-356711 https://www.duh.de/presse/pressemitteilungen/pressemitteilung/lng-terminal-in-mukran-deutsche-umwelthilfe-legt-widerspruch-gegen-aenderungsgenehmigung-ein/ https://www.offshore-energy.biz/german-player-picks-up-permanent-permit-for-lng-terminal-with-fsru-duo/ https://www.wartsila.com/energy/engine-power-plant-solutions/engine-power-plant-products/wartsila-50df-dual-fuel-engine https://www.enerdata.net/publications/daily-energy-news/deutsche-regas-terminates-contract-fsru-energos-power-germany.html
Piombino FSRU | T100000131096 | 4x internal-combustion engines/gensets (GE1-GE4) | 5.85 MW / 11.7 MW / 11.7 MW / 11.7 MW | 23.4 MW (2 largest running); ~41 MW installed | Aggregate >=20 MW (genset rule) | Reciprocating genset | https://va.mite.gov.it/File/Documento/678395 https://va.mite.gov.it/File/Documento/837896
Wilhelmshaven LNG Terminal (Wilhelmshaven 1) | T100000130458 | 4x Wartsila W8L50DF gensets | 7.8 MW each | 31.2 MW t+H9otal | Aggregate >=20 MW (genset rule) | Reciprocating dual-fuel genset | https://www.wilhelmshaven-lng.de/index.php/en/fsru https://www.asap.nl/hoegh-esperanza-fsru-flawless-lng-sampler-inspection/
Zeebrugge LNG Terminal | T100000130426 | CHP/WKK unit | n/a | 45,875 kVA (~37 MW electric, est.) | Aggregate >=20 MW (genset/CHP rule) | Gas-fired CHP (genset-class) | https://gpbv.omgeving.vlaanderen.be/api/view/vergunningsbesluiten/bestand?uniekeSleutel=a2526f5f-59a9-44db-8ec4-118c5bb28da7

## EU - Excluded
Terminal | Terminal ID | Reason Excluded | MW Figure (if any) | References
Alexandroupolis FSRU | T100000130681 | No MW figure disclosed | None | https://www.gastrade.gr/en/the-project/ https://www.gastrade.gr/en/sustainabilty/
Constanta LNG Terminal | T100000130502 | Below threshold (steam turbo-generators) | 18 MW total | http://energy-cie.ro/archives/2013/nr_3/v4-n3-5.pdf
Cyprus FSRU | T100000130432 | No MW figure disclosed | None | https://maritime-executive.com/article/first-fsru-for-cyprus-begins-commissioning-at-cosco-shipyard https://www.offshore-energy.biz/cosco-hands-over-first-fsru-to-cyprus/
Eemshaven FSRU | T100000130997 | No MW figure disclosed (standby-reclassified) | None | https://www.rvo.nl/sites/default/files/2022-12/OB01-Ontwerpbesluit-Omgevingsvergunning-EemsEnergy-Terminal.pdf
Etki FSRU | T100000130541 | No MW figure disclosed | None | https://www.etkiliman.com.tr/en/FSRU/FSRU.html
HIGAS LNG Terminal | T100000130724 | No MW figure disclosed | None | https://www.ogj.com/pipelines-transportation/lng/article/14198204/sardinia-lng-terminal-nears-completion https://www.rivieramm.com/news-content-hub/news-content-hub/reganosa-to-operate-new-italian-small-scale-lng-terminal-64474
Klaipeda FSRU | T100000130488 | No MW figure disclosed | None | https://ve.lt/verslas/klaipedos-sgd-terminalo-elektrifikacijos-projekte-svarbus-zingsnis-pradeti-pirmieji-darbai https://gargzdai.lt/kn-energies-issirinko-elektros-linijos-jungties-su-klaipedos-sgd-terminalu-projektavimo-ir-statybos-darbu-rangova/ https://www.offshore-energy.biz/lng-terminal-electrification-moving-forward-as-contractor-gets-shore-connection-job/ https://ceenergynews.com/lng/klaipeda-lng-terminal-contractor-electrification/ https://www.atviraklaipeda.lt/2025/10/24/pradeta-sgd-terminalo-elektrifikacija/
Krk FSRU | T100000130430 | Below threshold | 16.5 MW total | http://web.archive.org/web/20240905234117/https://hrcak.srce.hr/file/425010 https://www.lng.hr/en/about-the-terminal
Montoir LNG Terminal | T100000130456 | No MW figure disclosed (standby-reclassified) | None | https://www.georisques.gouv.fr/webappReport/ws/installations/document/f28699db1b6b4fa2b9211c28a7607ee6 https://www.georisques.gouv.fr/risques/installations/donnees/details/0006300974
Polish Baltic Sea Coast FSRU | T100000130731 | No MW figure disclosed | None | https://www.gaz-system.pl/dam/jcr:5e7b9dea-7e9b-4d4c-a759-92bbed766b4c/fsru-raport-o-oddzialywaniu-na-srodowisko-tom-i-streszczenie.pdf https://www.gaz-system.pl/pl/dla-mediow/komunikaty-prasowe/2026/maj/19-05-2026-jednostka-fsru-zwodowana-kolejny-kamien-milowy-strategicznej-inwestycji-gaz-system.html
Ravenna LNG Terminal | T100000130683 | No MW figure disclosed | None | https://va.mite.gov.it/File/Documento/905969 https://va.mite.gov.it/File/Documento/522381
Revithoussa LNG Terminal | T100000130462 | Below threshold | 13 MW total | https://www.desfa.gr/wp-content/uploads/2024/07/DESFA-LNG-Terminal-Revithoussa_.pdf
Taranto LNG Terminal | T100001084182 | Below threshold | ~3 MW (bifuel cogen, standby-reclassified) | https://va.mite.gov.it/File/Documento/1350130 https://va.mite.gov.it/File/Documento/1350095
Toscana FSRU | T100000130474 | Aggregate >=20 MW (onboard steam-turbogenerator plant, BOG-fired; aggregate treatment is a judgment call - steam TGs are neither aeroderivative nor gensets, cf. the Constanta exclusion, but as a self-contained offshore island plant the fleet aggregates like a genset set) | 10 MW (largest units); 3.35 MW (smaller pair). 26.7 MW total gas-fired. Onboard BOG-fired steam power plant aboard FSRU Toscana: boilers normally burning boil-off gas feed 2x10 MW plus 2x3.35 MW steam turbogenerators; the terminal is energy self-sufficient ~22 km offshore with no shore-power connection (diesel gensets emergency-only). | https://va.mite.gov.it/File/Documento/135472 https://va.mite.gov.it/File/Documento/42972
Trieste Monfalcone LNG Terminal | T100000130482 | Cancelled - excluded per instruction. 2006 EIA design: offshore GBS terminal energy self-sufficient via 3 gas-turbine-driven electric generators (~16 MW each, 2 duty + 1 spare), diesel sets startup/emergency only - would qualify on aggregate if active. | ~48 MW installed / ~32 MW duty (3x~16 MW, design) | https://va.mite.gov.it/File/Documento/3068
Zaule LNG Terminal | T100000130484 | No MW figure disclosed | None | https://va.mite.gov.it/File/Documento/2489
Zeeland Energy FSRU (ZET) | T100000131099 | No MW figure disclosed; generators OFF during normal operation per design (standby-reclassified) | None | https://www.rvo.nl/sites/default/files/2025-12/Concept-NRD%20-%20Zeeland-Energy-Terminal-(ZET).pdf

## Russia - Qualifying (>=50MW)
Terminal | Terminal ID | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | Turbine/Genset Class | References
Arctic LNG 2 Terminal | T100000130520 | CGT30 gensets (electric, Wison-built) + 4x Baker Hughes LM9000 (mechanical drive, Train 1) | LM9000 >65 MW each at shaft | 1,500 MW electric (3x500MW stages); LM9000 aggregate ~260-290 MW shaft | Qualifies both ways (individual AND aggregate) | Aeroderivative (LM9000) + industrial (CGT30) | https://interfax.com/newsroom/top-stories/90530/ https://www.highnorthnews.com/en/undeterred-sanctions-novatek-begins-production-arctic-lng-2 https://en.highnorthnews.com/business/china-to-supply-key-turbines-to-novateks-arctic-lng-2/157312 https://en.highnorthnews.com/business/russias-novatek-on-track-to-complete-2nd-train-of-arctic-lng-2-in-2024/202782
Sakhalin II LNG Terminal | T100000130512 | 4x GE Frame 7EA (mechanical drive, process trains) | ~85-90 MW each (Frame 7EA class) | n/a (mechanical drive, not summed) | Individual >=50 MW | Industrial gas turbine (mechanical drive) | https://www.ge.com/news/press-releases/ge-wins-333-million-service-contract-extension-sakhalin-2-lng-plant-subarctic-russia https://www.nsenergybusiness.com/projects/sakhalin-2-oil-and-gas-project/
Ust Luga LNG Terminal | T100000130504 | 4x Mitsubishi H-100 gas turbines (mechanical drive) | 120 MW each | ~480 MW aggregate | Individual >=50 MW | Industrial gas turbine (mechanical drive) | https://power.mhi.com/news/20211125.html

## Russia - Excluded
Terminal | Terminal ID | Reason Excluded | MW Figure (if any) | References
Marshal Vasilevskiy FSRU | T100000130831 | No MW figure disclosed (2x Wartsila 12V50DF reciprocating gensets aboard the FSRU; plausibly could reach or exceed 50 MW aggregate depending on exact model rating, but unconfirmed in source data) | None | https://www.korabel.ru/fleet/info/60111.html
Obsky LNG Terminal | T100000130921 | Below 50 MW threshold (individual turbine rule applies; SGT-700 mechanical drive, not aeroderivative or genset) | 32.8 MW each (~230 MW aggregate, 7 units + 1 spare) | https://www.kommersant.ru/doc/4290335 https://www.tek-all.ru/news/id7693-gazovaya-turbina-serdtse-proekta-novatek-po-transportirovke-gaza-budet-kitayskoy/ https://bmpd.livejournal.com/4324161.html
Portovaya LNG Terminal | T100000130707 | Below 50 MW threshold (individual turbine rule applies; GPA-32 'Ladoga' mechanical drive, not aeroderivative or genset) | ~32 MW each at drive coupling (per train) | https://lngnews.ru/project/kspg-portovaya/ https://oilgascom.com/rep-xolding-otgruzil-oborudovanie-dlya-zavoda-spg-v-rajone-ks-portovaya/
Shtokman LNG Terminal | T100000130514 | Cancelled/frozen - excluded per instruction. Published design for the Teriberka LNG plant included a dedicated own-needs ('sobstvennykh nuzhd') gas-turbine power station of 600 MW using 110+ MW-class units (2009 construction tender); independent academic analysis corroborates the same solution class (4x GTE-110, 442 MW) - would qualify both ways if active. | 600 MW (design; 110+ MW-class units) | https://cyberleninka.ru/article/n/potentsial-energosberezheniya-gazoturbinnoy-elektrostantsii-pri-realizatsii-pervoy-stadii-shtokmanovskogo-proekta https://ru.thebarentsobserver.com/tender-na-stroitelstvo-elektrostancii-v-teriberke/300953
Yamal LNG Terminal | T100000130518 | Below 50 MW threshold (individual turbine rule applies; SGT-800 is a standard industrial gas turbine, not aeroderivative or genset, so aggregate does not apply) | 47 MW each (376 MW total) | https://www.power-technology.com/data-insights/power-plant-profile-yamal-lng-power-plant-russia/ https://energoseti.ru/station/yamal-spg-tes https://www.niiosp.ru/objects/0010/

## Americas - Qualifying (>=50MW)
Terminal | Terminal ID | Country | Status | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | References
Alaska LNG Terminal | T100000130206 | USA | proposed | On-site gas turbine generators (N+1 config), off-grid; separate mechanical-drive turbine-compressors (298,000 ISO hp, excluded from electric figure) | n/a (genset-style multi-unit config) | 124 MW electric | Aggregate >=50 MW (genset/off-grid rule) | https://dec.alaska.gov/media/21764/02-general-project-info-resource-report-1.pdf
Argent LNG Terminal | T100000131163 | USA | pre-construction | GOGPT-matched captive power plant | n/a | 675 MW | Aggregate/plant total >=50 MW | https://worldoil.com/news/2025/2/4/baker-hughes-to-provide-liquefaction-tech-for-argent-lng-24-mtpa-facility/ https://www.hydrocarbonengineering.com/gas-processing/04022025/argent-energy-selects-baker-hughes-as-technology-provider/
Argentina LNG Terminal | T100000130832 | Argentina | proposed (2 FLNG vessels committed: Hilli Episeyo 2027, MK II/Fuji LNG hull 2028) | Onboard steam-turbine-generators (waste heat recovery) + mechanical GE PGT25+G4/2BCL gas-turbine refrigerant compression (4 trains) | n/a | 66 MW electric (2x33 MW Peter Brotherhood steam turbine-generators) | Aggregate >=50 MW (genset/steam-turbine rule) | https://www.ge.com/news/press-releases/ge-technology-and-services-support-conversion-golar-lng-floating-liquefaction-vessel https://www.manualshelf.com/manual/ge/aeroderivative-gas-turbines-pgt25/brochure-english/page-1.html https://offshoreeuropejournal.com/news/fullstory.php/aid/8640/Turbine_order_secured.html https://www.golarlng.com/fleet.aspx https://www.offshore-technology.com/news/seatrium-flng-hilli-episeyo-upgrade/
Calcasieu Pass LNG Terminal | T100000130212 | USA | operating | GOGPT-matched captive power plant | n/a | 720 MW | Aggregate/plant total >=50 MW | https://www.ferc.gov/sites/default/files/2020-05/06-22-18-DEIS.pdf https://ventureglobal.com/calcasieu-pass/calcasieu-pass-facility/
Cameron LNG Terminal | T100000130214 | USA | operating (T1-3); proposed (T4) | Frame 7-class gas turbines shaft-driving the propane and mixed-refrigerant compressors on Trains 1-3 (mechanical drive, no electricity generated). Proposed Train 4 switches to 3x electric E-Drive motors (up to 75 MW each), so T4 itself is not captive. | ~85-90 MW shaft each (Frame 7 class; no site-specific figure published) | n/a (mechanical drive, not summed) | Individual >=50 MW (mechanical drive) | https://cameronlng.com/lng-facility/lng-and-liquefaction/ https://gascompressionmagazine.com/2022/03/21/cameron-lng-expansion-requests-train-4-enhancement/
Commonwealth LNG Terminal | T100000130215 | USA | construction | GOGPT-matched captive power plant; mechanical-drive turbines also drive compressors | n/a | 438.6 MW | Aggregate/plant total >=50 MW | https://www.energy.gov/sites/default/files/2022-09/final-eis-0533-vol1-commonwealth-lng-2022-09_0.pdf https://web.archive.org/web/2024/https://www.offshore-technology.com/projects/commonwealth-lng-terminal-louisiana-usa/
Corpus Christi LNG Terminal | T100000130216 | USA | operating (T1-3); construction/proposed (Stage 3) | GE LM2500+G4 / Baker Hughes PGT25+G4 aeroderivative gas turbines mechanically driving the propane/ethylene/methane refrigerant compressors on Trains 1-3 (Optimized Cascade). Stage 3 reportedly shifts to motor-driven compressors. | ~34 MW shaft each (LM2500+G4 class) | 18 drivers across T1-3 (~600 MW shaft class) | Aggregate >=50 MW (aeroderivative rule; mechanical drive) | https://archive.epa.gov/region6/6pd/air/pd-r/ghg/web/pdf/corpuschristi-liq-turbine-simple-cycle060613.pdf https://www.bakerhughes.com/company/news/bhge-wins-turbomachinery-contract-cheniere-energy-incs-lng-facility-corpus-christi
Cove Point LNG Terminal | T100000130217 | USA | operating | 2x GE Frame 7EA mechanical-drive + waste-heat 2x65 MW steam turbine generators (bottoming plant) | 65 MW each (steam turbine-generators) | 130 MW (steam bottoming plant); 210.9 MW total on-site nameplate incl. legacy units | Qualifies both ways (individual AND aggregate) | https://dnr.maryland.gov/pprp/Documents/Dominion_Energy_Cove_Point_Fact_Sheet.pdf https://aglaw.psu.edu/wp-content/uploads/2021/02/Cove-Point-FERC-Certificate-9.29.14.pdf https://www.ge.com/news/press-releases/ge-technology-power-dominions-cove-point-lng-liquefaction-project-maryland
CP2 LNG Terminal | T100000130973 | USA | construction; pre-construction | GOGPT-matched captive power plant | n/a | 2,190 MW | Aggregate/plant total >=50 MW | https://www.energy.gov/sites/default/files/2023-08/eis-0551-venture-global-cp2-lng-feis-2023-07-01.pdf https://lngprime.com/americas/venture-global-gets-pre-filing-waiver-for-cp2-lng-expansion/183889/
Firebird LNG Terminal | T100000131139 | Suriname | proposed (EPC contract signed 2022) | Siemens SCC6-800 6x1 combined-cycle power island (6 gas turbines + 6 HRSGs + 1 steam turbine) | n/a | 430 MW | Aggregate >=50 MW (combined-cycle genset rule) | https://www.lawinsider.com/contracts/emRNz0M0sxz https://oilnow.gy/featured/mega-lng-deep-water-port-for-suriname-up-for-environmental-authorisation/ https://portofnickerie.com/en/lng-facility-en/
Freeport LNG Terminal | T100000130224 | USA | operating | Dedicated gas-turbine generator at the on-site Pretreatment Facility (Quintana, TX), normally fueled by boil-off gas piped from the liquefaction plant, with waste-heat recovery to the three pretreatment trains. The main T1-T4 liquefaction trains are electric-motor-driven (3x 75 MW GE motors per train) and grid-fed via ERCOT - NOT captive. | ~50 MW (nameplate not disclosed; the unit exported ~50 MW to ERCOT during the Jun-Oct 2022 outage while normally also carrying house load, so nameplate is at least ~50 MW) | ~50 MW (single unit) | Individual ~>=50 MW (observed grid export; nameplate undisclosed - borderline, flagged for review) | https://freeportlng.com/index.php?p=our-business/elng/ https://gasprocessingnews.com/news/2022/07/freeport-lng-plant-pulls-in-natgas-to-produce-power-for-texas/ https://www.epa.gov/sites/default/files/2018-03/documents/tx0134056_statement_of_basis.pdf
Golden Pass LNG Terminal | T100000130227 | USA | operating; construction | Six GE/Baker Hughes MS7001EA (Frame 7EA) heavy-duty gas turbines shaft-driving 12 refrigerant compressors across 3 trains; BOG compression on separate ~6.8 MW electric motors. | ~85-90 MW shaft each (Frame 7EA class) | n/a (mechanical drive, not summed) | Individual >=50 MW (mechanical drive) | https://www.bakerhughes.com/company/news/baker-hughes-ge-company-supply-turbomachinery-equipment-golden-pass-lng-export https://www.hydrocarbonengineering.com/tanks-terminals/11022019/bhge-to-supply-turbomachinery-equipment-for-golden-pass-lng-export-facility/
Gulfstream LNG Terminal | T100000131128 | USA | pre-construction | GOGPT-matched captive power plant | n/a | 275 MW | Aggregate/plant total >=50 MW | https://www.hydrocarbonprocessing.com/news/2024/05/gulfstream-lng-export-terminal-us-receives-us-ferc-approval/ https://lngprime.com/americas/gulfstream-lng-asks-us-ferc-to-start-pre-filing-process/110112/
Ksi Lisims FLNG Terminal | T100000130914 | Canada | proposed (permanent design is BC Hydro grid-tied; gas-turbine plant is a contingency) | CONTINGENT DESIGN ONLY: 8 gas turbine generator sets in combined cycle with steam turbines (temporary floating power barges, up to 5 years if grid interconnection delayed) | n/a | 603 MW net (contingent scenario) | Aggregate >=50 MW (genset rule) -- CONTINGENT, not primary design | https://projects.eao.gov.bc.ca/api/public/document/66d0bd026e43500022c60766/download/03_KsiLisimsLNG_1_Project_Overview_Final.pdf https://projects.eao.gov.bc.ca/api/public/document/66d0fd0f51493a0022ff113a/download/34_K https://www.theglobeandmail.com/business/article-ksi-lisims-lng-decision-construction-bc-energy-project/
LNG Canada Terminal | T100000130358 | Canada | operating/construction (phased) | GE LMS100 aeroderivative gas turbines (2 per train) mechanically driving refrigerant compressors; ~20% of power from BC Hydro | 93.4 MW each | n/a (mechanical drive, per-unit) | Individual >=50 MW (aeroderivative) | https://www.lngcanada.ca/who-we-are/about-lng-canada/ https://jfjvkitimat.com/wp-content/uploads/2023/07/Waste_Discharge_Authorization_Permit_for_Air_Emissions-compressed.pdf https://www.ge.com/news/press-releases/lng-canada-selects-ge-oil-gas-high-efficiency-lms100-gas-turbine-compressor-0 https://projects.eao.gov.bc.ca/api/document/5886905ce036fb0105768a9b/fetch/Greenhouse%20Gas%20Management%20Technical%20Data%20Report.pdf
Magnolia LNG Terminal | T100000130234 | USA | proposed | Two 33 MW gas turbines per liquefaction train directly driving the mixed-refrigerant compressors (OSMR; mechanical drive). On-site electricity generation explicitly ruled out in design; remaining 6.5 MW/train electrical load grid-fed via a new 230-kV Entergy line. | 33 MW shaft each | 66 MW shaft per train; 264 MW across 4 trains | Aggregate >=50 MW (mechanical drive) | https://www.energy.gov/sites/default/files/2015/11/f27/EIS-0498_Magnolia_LNG_FEIS_%28Nov_2015%29.pdf
New Fortress Altamira LNG Terminal | T100000131069 | Mexico | Pioneer III platform: 3x ~11 MW Siemens SGT-400 simple-cycle gensets (electric); Pioneer II platform: 1x Baker Hughes LM6000PF+ (aeroderivative, mechanical drive on IPSMR refrigerant compressor) | Pioneer III aggregate ~33 MW (below 50); Pioneer II individual MW not disclosed in source (LM6000PF+ mechanical-drive ratings are commonly in the ~44-50 MW class but no source-confirmed figure exists here) | Two separate off-grid platforms, both entirely captive (no shore/CFE connection per DOE EA and company materials), but neither disclosed figure clearly and confidently clears 50 MW on its own. |  | Exclude under a strict 'confirmed figure only' reading; include if a reasonable LM6000PF+ typical rating (~44-50 MW) is treated as sufficient evidence. Recommend a targeted follow-up search on the specific LM6000PF+ unit's nameplate rating before deciding. | https://www.energy.gov/sites/default/files/2023-12/Final%20Environmental%20Assessment%20-%20NFE%20Altamira%20FLNG_12.12_2023%20With%20errata.pdf https://www.newfortressenergy.com/stories/altamira-fast-lng-1-brings-positive-energy-mexico https://gascompressionmagazine.com/2024/07/26/fast-lng-achieves-first-lng/ https://www.newfortressenergy.com/stories/three-cheers-three-fast-lng-rigs-installed-altamira-mexico
Penuelas LNG Terminal (EcoElectrica) | T100000130578 | Puerto Rico (USA) | operating | 2x gas-turbine-driven generators (205 MVA @ 0.85pf each) + 1x steam-turbine generator (252 MVA @ 0.85pf, not gas-turbine driven) | ~174.25 MW each (gas-turbine-driven units only) | ~348.5 MW (2 gas-turbine units) + 214.2 MW steam unit | Qualifies both ways (individual AND aggregate) -- gas-turbine-driven units only | https://www.ccj-online.com/4q-2012/plant-report-ecoelectrica-lp/ https://drna.pr.gov/wp-content/uploads/2020/01/Ecoelectrica-English-TV-4911-57-0899-0006.pdf https://www.ferc.gov/sites/default/files/2020-06/C-4-061820.pdf https://energia.pr.gov/wp-content/uploads/sites/7/2020/05/2020-05-19-Reply-EcoElectrica-PPOA-PREPA-PREB-FINAL-VERSION-with-Exhibit.pdf
Peru LNG Terminal (Pampa Melchorita) | T100000130576 | Peru | operating | GE Frame 7/MS7001/7EA mechanical-drive refrigeration compressors + 3x GE LM2500+ aeroderivative gas turbine-generators (electric) | ~85-90 MW each (Frame 7EA, mechanical drive); LM2500+ individually ~30-34 MW | ~90-100 MW aggregate (3x LM2500+ generators) | Qualifies both ways: Frame 7EA individual >=50 MW (mechanical); LM2500+ aggregate >=50 MW (aeroderivative) | https://www.ge.com/news/press-releases (GE 2015 long-term service agreement release, exact URL not preserved in source workbook) McDermott project page (exact URL not preserved in source workbook)
Plaquemines LNG Terminal | T100000130242 | USA | construction; operating; pre-construction | GOGPT-matched captive power plant | n/a | 2,860 MW | Aggregate/plant total >=50 MW | https://ventureglobal.com/venture-global-plaquemines/plaquemines-facility/ https://web.archive.org/web/2024/https://www.offshore-technology.com/projects/plaquemines-lng-project-louisiana/
Port Arthur LNG Terminal | T100000130237 | USA | construction | FERC-certified on-site gas-turbine generator fleet (240 MW) PLUS four GE Frame 7 gas turbines mechanically driving the eight main refrigerant compressors (Phase 1). | Generators not broken out; Frame 7 mechanical drives ~85 MW shaft class each | 240 MW (FERC-certified generation) | Qualifies both ways (aggregate generation AND individual mechanical drive) | https://www.ferc.gov/sites/default/files/2020-04/C-3.pdf https://www.lngindustry.com/liquefaction/28032023/baker-hughes-to-supply-liquefaction-trains-for-sempra-infrastructures-port-arthur-lng-phase-1-project/
Rio Grande LNG Terminal | T100000130239 | USA | construction (T1-5); proposed (expansion) | Frame 7 heavy-duty gas turbines directly coupled to the main refrigerant compressors across Trains 1-5 (Optimized Cascade); no electric-drive/grid language in any source. | ~85-90 MW shaft each (Frame 7 class; no project-specific figure published) | n/a (mechanical drive, not summed) | Individual >=50 MW (mechanical drive) | https://www.globenewswire.com/news-release/2025/09/11/3148922/0/en/Baker-Hughes-Secures-Order-for-Rio-Grande-LNG-Expansion.html https://www.lngindustry.com/liquefaction/15092025/baker-hughes-to-supply-main-liquefaction-equipment-for-rio-grande-lng-expansion/ https://www.worldoil.com/news/2025/11/6/baker-hughes-wins-order-for-nextdecade-s-rio-grande-lng-train-5-expansion/
Sabine Pass LNG Terminal | T100000130240 | USA | operating; pre-construction | GOGPT-matched captive power plant; mechanical-drive turbines also drive compressors | n/a | 1,665.6 MW | Aggregate/plant total >=50 MW | https://www.energy.gov/sites/prod/files/EA-1845-FEA-2011.pdf https://www.epa.gov/sites/default/files/2015-08/documents/sabinepass_petition2012.pdf
ST LNG FLNG Terminal | T100001061236 | USA | proposed | Off-grid by design (MARAD DWP application): 16x Baker Hughes NovaLT16 gas turbine generators project-wide (4/phase incl. one standby) plus 8x Siemens SGT-750 gas turbines as MR compressor mechanical drives. | 16.9 MW each (NovaLT16) | 270.4 MW installed generation (~202.8 MW at normal N+1 load), plus 8x SGT-750 mechanical drive | Aggregate >=50 MW (genset-style generator fleet; also mechanical drive) | https://downloads.regulations.gov/MARAD-2025-0096-0001/attachment_1.pdf https://downloads.regulations.gov/MARAD-2025-0096-0028/attachment_1.pdf
Woodside Louisiana LNG Terminal | T100000130219 | USA | construction | GOGPT-matched captive power plant; mechanical-drive turbines also drive compressors | n/a | 430.4 MW | Aggregate/plant total >=50 MW | https://www.ferc.gov/sites/default/files/2020-05/01-18-19-FEIS.pdf https://www.lngindustry.com/liquefaction/03012025/baker-hughes-secures-liquefaction-equipment-order-for-woodside-louisiana-lng/

## Americas - Excluded
Terminal | Terminal ID | Country | Reason Excluded | MW Figure (if any) | References
Atlantic LNG Terminal | T100000130579 | Trinidad and Tobago | No confirmed aggregate MW -- Solar Mars 100 gas-turbine generator sets confirmed to exist (at least 4 for Train 4 plus a pre-existing fleet for Trains 1-3) but no source discloses the aggregate nameplate MW of that generating fleet | Individual Solar Mars 100 units are a well-known ~11.4 MW class turbine, but no aggregate figure confirmed | ConocoPhillips/Bechtel technical paper (LNG14, Doha, March 2004); GE Oil & Gas Train 1 compressor-upgrade release
Aurora LNG Terminal | T100000130346 | Canada | Cancelled - excluded per instruction. 2014 federal Project Description: gas-turbine-driven refrigerant compressors plus likely on-site gas-fired self-generation (est. 120-300 MW Phase 1 / 200-550 MW full build; type/capacity was to be set in FEED). | est. 120-550 MW (design estimate only) | https://iaac-aeic.gc.ca/050/documents/p80075/99505E.pdf
Bahia Blanca GasPort FSRU | T100000130538 | Argentina | No MW figure disclosed (and idled). FSRU Excelerate Excelsior onboard dual-fuel engines burning predominantly LNG/BOG per Excelerate fleet-wide disclosure (FSRU-onboard convention). | None | https://excelerateenergy.com/our-operations/floating-lng-terminals/ https://excelerateenergy.com/wp-content/uploads/2025/08/Excelerate-Energy-2024-SR-080125.pdf
Bahia FSRU | T100000130925 | Brazil | No MW figure disclosed. FSRU Excelerate Sequoia onboard dual-fuel generating plant run predominantly on BOG per Excelerate fleet-wide disclosure (FSRU-onboard convention). | None | https://excelerateenergy.com/projects/bahia-brazil-tr-ba/ https://excelerateenergy.com/wp-content/uploads/2025/08/Excelerate-Energy-2024-SR-080125.pdf
Bear Head LNG Terminal | T100000130347 | Canada | Cancelled - excluded per instruction. OSMR design (sister project to Magnolia LNG): aero-derivative gas turbines driving the refrigeration compressors plus a CHP plant for facility power. No MW disclosed. | None disclosed | https://www.offshore-technology.com/projects/bear-head-lng-project-richmond-county-nova-scotia/
Cartagena FSRU (Colombia) | T100000130562 | Colombia | No MW figure disclosed. FSRU Hoegh Grace built with Wartsila-Hyundai DFDE generating engines (FSRU-onboard convention). | None | https://www.marineinsight.com/hoegh-lng-takes-delivery-of-ninth-fsru-hoegh-gannet/ https://www.offshore-energy.biz/hoegh-lng-names-6th-fsru-at-hhi/
Coastal Bend LNG Terminal | T100001061247 | USA | No confirmed MW figure -- 'cogeneration' is named as a design element but no nameplate capacity or unit count has been published by the single-publisher source (developer's own site) | None disclosed | coastalbendlng.com (developer's own site, single publisher)
Cosan FSRU | T100000130927 | Brazil | No MW figure disclosed. FSRU Hoegh Giant onboard generating plant, gas-capable per Hoegh Evi's fleet-wide disclosure (FSRU-onboard convention; fleet-wide claim, not vessel-specific spec). | None | https://hoeghevi.com/about/fleet/ https://hoeghevi.com/sustainability/environment/
Costa Azul LNG Terminal | T100000130810 | Mexico | No confirmed MW figure for the on-site power generation unit (Unit 71); mechanical-drive liquefaction turbines confirmed but not electric captive generation capacity | None disclosed for Unit 71 (Unit 72 is emergency-only, excluded from captive) | Mexican environmental-authorization filing for the Costa Azul liquefaction addition
Delfin FLNG Terminal | T100000130218 | USA | Four Siemens SGT-750 Gas Turbine (42.2 MW each in mechanical drive) Mechanical Drive Packages which will be used to drive the mixed-refrigerant compressors for Delfin’s LNG liquefaction system. These are not aeroderivative GTs. | 168.8 MW | https://www.energy.gov/sites/prod/files/2018/11/f57/final-eis-0531-port-delfin-lng-main-volume-2016-11.pdf https://www.energy.gov/sites/default/files/2024-03/Attachment%201%20Delfin%20LNG%20Design%20Update%20%2014June2022.pdf
Delta LNG Terminal | T100000130985 | USA | Cancelled/withdrawn (June 2025, in favor of expanding adjacent Plaquemines LNG) - excluded per instruction. Published design named a dedicated on-site 'gas-powered power plant' as a distinct component, but no turbine model, unit count, or MW rating was found in any verifiable source. | None disclosed | https://www.offshore-technology.com/news/venture-global-withdraws-delta-lng-project/
Elba Island LNG Terminal | T100000130221 | USA | Below 50 MW threshold -- only reclassified to YES under a broadened 'any turbine that runs when grid fails counts' directive; actual on-site combustion generators are 2 RICE + 2 gas turbines at ~2.8-2.9 MW class each (~11.2 MW aggregate), permitted as emergency/backup only (<500 hr/yr) | ~11.2 MW aggregate (emergency/backup units only) | Georgia EPD PSD Preliminary Determination
Escobar FSRU | T100000130542 | Argentina | No MW figure disclosed. FSRU Excelerate Expedient onboard dual-fuel engines burning predominantly LNG/BOG per Excelerate fleet-wide disclosure (FSRU-onboard convention). | None | https://excelerateenergy.com/our-operations/floating-lng-terminals/ https://excelerateenergy.com/wp-content/uploads/2025/08/Excelerate-Energy-2024-SR-080125.pdf
G2 LNG Terminal | T100000130226 | USA | Cancelled - excluded per instruction. Design integrated a NET Power Allam-Fetvedt gas-fired power island (300 MW per module, >1,000 MW across the full build) - would qualify on aggregate if the project were active. | 300 MW per module (design; >1,000 MW full build) | https://lngprime.com/americas/g2-net-power-ink-new-deal-for-louisiana-lng-export-project/19753/ https://www.lngindustry.com/special-reports/11052021/g2-and-net-power-collaborate-on-net-zero-lng-project/ https://www.offshore-energy.biz/g2-advances-its-net-zero-lng-export-project/
Goldboro LNG Terminal | T100000130354 | Canada | Cancelled - excluded per instruction. NS Environmental Assessment registration listed a dedicated 180 MW open-cycle gas-turbine power plant (Frame 6, N+1) feeding electric-motor-driven compressors, plus separate Frame 7 mechanical-drive turbines (~160 MW class) on the two trains - would qualify if active. | 180 MW plant (design) + Frame 7 mechanical drive | https://novascotia.ca/nse/ea/goldboro-lng/00-Executive-Summary.pdf https://novascotia.ca/nse/ea/goldboro-lng/03-Project-Description.pdf https://novascotia.ca/nse/ea/goldboro-lng/goldboro-panel-report-2014-03-07.pdf
Grand Isle Deepwater Port Terminal | T100000131129 | USA | Cancelled - excluded per instruction. 2023 MARAD deepwater-port license application: no grid connection; simple-cycle gas turbine generators would supply all facility power. No MW rating disclosed. | None disclosed | https://downloads.regulations.gov/MARAD-2023-0119-0003/attachment_5.pdf
Guanabara Bay FSRU | T100000130546 | Brazil | No MW figure disclosed. FSRU Excelerate Experience onboard dual-fuel generating plant run predominantly on BOG per Excelerate fleet-wide disclosure (FSRU-onboard convention). | None | https://excelerateenergy.com/projects/guanabara-bay-lng-import-terminal/ https://excelerateenergy.com/wp-content/uploads/2025/08/Excelerate-Energy-2024-SR-080125.pdf
Gulf LNG Terminal | T100000130228 | USA | Below threshold - the operating import terminal is grid-fed (Mississippi Power, 23 kV) with only two 12 MW essential-backup gas turbine generators on site. The FERC-authorized liquefaction expansion (never built) would add four mechanical-drive gas turbines (two per train), but no MW rating is disclosed in any verified source. | 24 MW (2x12 MW backup GTGs at the import terminal) | https://www.energy.gov/sites/prod/files/2019/04/f62/final-eis-0504-gulf-lng-2019-04-chp-2.pdf https://www.ferc.gov/sites/default/files/CalendarFiles/20190716201154-CP15-521-000.pdf https://www.nsenergybusiness.com/projects/kinder-morgans-gulf-lng-export-project/
Jordan Cove LNG Terminal | T100000130230 | USA | Cancelled - excluded per instruction. FERC FEIS design: direct-drive gas turbines on the refrigeration compressors with waste-heat recovery (HRSG) feeding a steam turbine-generator for facility power (superseded the earlier 420 MW South Dunes combined-cycle concept). No MW rating disclosed for the final design. | None disclosed (earlier concept: 420 MW CCGT) | https://www.ferc.gov/sites/default/files/2020-05/11-15-19-FEIS_Part_1.pdf
Kenai LNG Terminal | T100000130231 | USA | Historic mechanical-drive Frame 5 turbines (1969-era) are now mothballed and not part of the current proposed design; the current Trans-Foreland Cool Down import-conversion design adds only a 1,000-hp electric BOG booster compressor, far below the 50 MW threshold | Historic: Frame 5 (not disclosed, mothballed); Current design: <1 MW electric | Oil & Gas Journal; ConocoPhillips liquefaction-technology paper (original designer/operator)
Kwispaa LNG Terminal | T100000130366 | Canada | Cancelled - excluded per instruction. BC EAO Initial Project Description described an on-site gas-fired power generation facility (up to ~500 MW per 12-mtpa phase, ~1,000 MW full build) as one of two co-equal power options (the other: BC Hydro grid); choice not finalized when cancelled. | up to ~500-1,000 MW (design option, not selected) | https://projects.eao.gov.bc.ca/api/document/5be33b1e578b640024f5d4ac/download
Lake Charles LNG Terminal | T100000130232 | USA | Shelved project - excluded per instruction. As-designed, the export trains use on-site gas turbines to mechanically drive the MR compressors (no on-site generation; facility load grid-fed via a new 230-kV Entergy line, diesel-only standby gensets). No turbine MW disclosed. | None disclosed (mechanical drive) | https://www.energy.gov/sites/prod/files/2015/08/f26/EIS-0491-FEIS-2015.pdf
Main Pass Energy Hub FLNG Terminal | T100000130636 | USA | Cancelled - excluded per instruction. Baker Hughes LM9000 aeroderivative gas turbines selected (2018) for the 2x Liqui-Max FLNG vessels; unit count and electric rating for this project never published. | LM9000 class ~65-73 MW each (class rating only) | https://www.bakerhughes.com/gas-turbines/aeroderivative-technology/lm9000-aeroderivative-gas-turbine https://www.lngindustry.com/liquid-natural-gas/26062018/gls-advances-mpeh-lng-export-project/ https://www.offshore-energy.biz/gls-selects-bhge-gas-turbines-for-its-main-pass-lng-project/
Manzanillo (Dominican Republic) LNG Terminal | T100000131094 | Dominican Republic | No MW figure disclosed. FSRU Energos Freeze onboard steam-turbine plant with dedicated high-pressure BOG compressors (boilers fired on boil-off gas) per Energos Infrastructure's fleet page (vessel- and site-specific; FSRU-onboard convention). The 2x430 MW + 414 MW onshore plants it feeds are fuel-supply-OUT, not captive. | None (onboard); onshore customer plants are not captive | https://bankinformationcenter.org/project/manzanillo-gas-power-s-a/ https://energosinfra.com/fleet https://lngprime.com/americas/nfe-seals-dominican-fsru-charter-deal/150997/ https://www.newsfilecorp.com/release/292153/Energia-2000-Commissions-414-MW-Manzanillo-Power-Plant-in-Dominican-Republic
Neptune LNG Terminal | T100000130633 | USA | Below threshold (and mothballed). EPA deepwater-port application documents the shuttle/regas vessels' onboard dual-fuel power-generation engines, 2x11,400 kW, operable in gas mode. | 22.8 MW (2x11.4 MW) | https://www.epa.gov/caa-permitting/permit-documents-neptune-deepwater-port-federal-waters-massachusetts-bay-lng https://www.epa.gov/sites/default/files/2015-08/documents/ndp-application.pdf
New Fortress Barcarena FSRU | T100000130926 | Brazil | No MW figure disclosed. FSRU Energos Celsius runs Wartsila TFDE (tri-fuel diesel-electric) generator sets with a BOG recondenser per Energos Infrastructure's own fleet page (vessel-specific; FSRU-onboard convention). | None | https://energosinfra.com/fleet https://www.marinelink.com/news/new-fortress-energy-takes-delivery-510361 https://www.sec.gov/Archives/edgar/data/1749723/000174972324000011/nfe-20231231.htm
Northeast Gateway FSRU | T100000130632 | USA | No MW figure disclosed (and idled). EBRV vessels carry onboard steam turbine generators fed by MHI dual-fuel boilers burning boil-off/natural gas during regas operations. | None | https://www.epa.gov/caa-permitting/permit-documents-northeast-gateway-energy-bridge https://www.epa.gov/sites/default/files/2015-08/documents/ngeb-application.pdf
Ocean Cay LNG Terminal | T100000130544 | Bahamas | Cancelled - excluded per instruction (also below threshold). Design: three 15 MW gas-fired turbine generators for the facilities' own power; project abandoned by 2009 at the design/EIA stage. | 45 MW (3x15 MW, design) | https://www.offshore-technology.com/projects/oceancaylngterminala/
Old Harbour FSRU | T100000130684 | Jamaica | No MW figure disclosed. FSRU Hoegh Gallant, gas-capable per Hoegh Evi's fleet-wide disclosure (FSRU-onboard convention; fleet-wide claim). The three downstream customer plants (190 MW JPS Old Harbour etc.) are fuel-supply-OUT, not captive. | None | https://hoeghevi.com/about/fleet/ https://hoeghevi.com/sustainability/environment/ https://jpt.spe.org/excelerate-buys-new-fortress-jamaican-assets-for-1-billion https://lngprime.com/americas/hoegh-gallant-fsru-ready-to-start-jamaica-job/34879/
Pacific NorthWest LNG Terminal | T100000130363 | Canada | Cancelled - excluded per instruction. Federal EA Decision Statement condition 3.1.5 mandated aero-derivative gas turbines driving the refrigerant compressors (mechanical drive). No MW disclosed. | None disclosed (mechanical drive) | http://web.archive.org/web/20170802063139/http://www.pacificnorthwestlng.com/media/PNW_fsAirQuality_V3.pdf https://iaac-aeic.gc.ca/050/evaluations/document/115669
Placentia Bay FLNG Terminal (Grassy Point) | T100000131042 | Canada | Effectively abandoned/shelved -- excluded per instruction. Newfoundland and Labrador cancelled the project's Crown Lands application in Nov 2023; independent 2025 reporting confirms the project website is down, it has been removed from NRCan's list of active Canadian LNG projects, and a competing 2025 proposal (Fermeuse Energy FLNG) explicitly notes Placentia Bay 'did not move forward.' Not formally labelled 'cancelled' in the source workbook, but treated as such here given the weight of independent evidence. | ~120-140 MW (contingent/base-case design, project since shelved) | https://www.rivieramm.com/news-content-hub/news-content-hub/new-lng-export-facility-proposed-for-eastern-canada-68139 ; Investors for Paris Compliance May 2025 report (project website down, removed from NRCan list)
Port Pelican LNG Terminal | T100000130647 | USA | Cancelled - excluded per instruction. Deepwater Port License Application specified three LM2000 gas-turbine generators (BOG-fueled, one as backup) as main power at 13.8 kV; diesel gensets emergency-only. | ~18 MW class x3 (~54 MW aggregate, class rating - not project-stated) | https://downloads.regulations.gov/USCG-2002-14134-0002/attachment_1.pdf
Prince Rupert LNG Terminal | T100000130364 | Canada | Cancelled - excluded per instruction. IAAC project description: gas-turbine mechanical-drive compression (~540 MW shaft class) plus separate on-site gas-turbine generation for plant electrical load (fully islanded design). | ~540 MW shaft class (design) | https://www.iaac-aeic.gc.ca/050/documents/p80042/88546E.pdf
Sergipe FSRU | T100000130664 | Brazil | No MW figure disclosed. FSRU Energos Nanook fitted with Wartsila DFDE generation per the operator's fleet spec page (FSRU-onboard convention). Separate from the 1,500 MW Porto de Sergipe CCGT the terminal supplies (fuel-supply-OUT, not captive). | None | https://energosinfra.com/fleet-assets/
Sinolam LNG Terminal | T100000131082 | Panama | Shelved - excluded per instruction (also no MW disclosed). FSU GasLog Singapore (TFDE LNG carrier conversion): onboard tri-fuel diesel-electric gensets, gas-capable (FSU-onboard convention). The downstream Sinolam Smarter Energy plant is fuel-supply-OUT, not captive. | None | https://www.bairdmaritime.com/shipping/tankers/gas/gaslog-wins-10-year-charter-in-panama-for-lng-fsu

## Asia - Qualifying (>=50MW)
Terminal | Terminal ID | Country | Status | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | References
Brunei LNG Terminal | T100000130273 | Brunei | operating | On-site fuel-gas-fired energy system at the Lumut plant (nine steam boilers, described by the operator as 'equivalent to a 300 MW power station') driving both mechanical-drive turbine-compressors and generator turbines; co-located 246 MWe Lumut Cogen Power Station, gas-fired, commissioned 1987, operated by Brunei LNG Sdn Bhd itself, supplies electricity and steam to the site. | 246 MWe (Lumut Cogen Power Station, single gas-fired cogen plant, operator-owned) | ~300 MW-equivalent for the boiler-driven energy system per the operator's own description, plus the separate 246 MWe cogen plant | Individual >=50 MW - the co-located 246 MWe Lumut Cogen Power Station, gas-fired and operated by Brunei LNG itself, individually clears the threshold many times over; the boiler-driven mechanical-drive/generator-turbine system (operator-described as 'equivalent to a 300 MW power station') also qualifies. | https://bruneilng.com/the-plant/, https://globalenergyobservatory.org/geoid/45546
Tianjin LNG Terminal (PipeChina) | T100000130410 | China | operating (current chartered FSRU service); retired and construction also recorded among unit-level statuses in the GEM export | FSRU onboard generator fleet: 3x11,400 kW + 1x5,700 kW dual-fuel gensets, plus 2x13,200 kW turbo/electric generators fed by dual-fuel main boilers (mainly natural gas, secondary low-sulfur diesel); a separate 500 kW emergency diesel genset is non-gas and excluded from the total. | 13.2 MW max individual unit (turbo/electric generator); largest genset is 11.4 MW - no single unit reaches 50 MW | 66.3 MW aggregate across gas-fired units (3x11.4+1x5.7 MW gensets = 39.9 MW, plus 2x13.2 MW turbo-generators = 26.4 MW; the 500 kW emergency diesel is excluded) | Aggregate >=50 MW (genset rule) - dual-fuel gensets and boiler-fed turbo/electric generators aboard the FSRU total 66.3 MW gas-fired capacity, well above the 50 MW aggregate threshold; individual units are all well under 50 MW. | https://www.mee.gov.cn/ywgz/hjyxpj/jsxmhjyxpj/xmslqk/201605/W020160522142436760339.pdf
Karaikal FSRU | T100000130803 | India | proposed | 3x22 MW gas turbine generators (66 MW aggregate) with SCR NOx control and waste heat recovery units, described as coming 'as part of the FSU' - the floating storage unit's own onboard power plant, for the proposed Karaikal LNG terminal. | 22 MW each - below the 50 MW individual threshold | 66 MW aggregate (3x22 MW gas turbine generators) | Aggregate >=50 MW (aeroderivative/genset-style rule applied by analogy to 3 parallel mid-size gas turbine generator units) - JUDGMENT CALL: the source does not state whether these are heavy-duty single-train turbines (individual-unit rule) or aeroderivative/genset-style redundant units (aggregate rule); flagged for review. | https://environmentclearance.nic.in/writereaddata/Form-1A/EC/11082018119327KaraikalPortECLetter.PDF
West Papua FLNG Terminal | T100000131148 | Indonesia | construction | Wison New Energies standard FLNG design: 2xLM6000PF+ aeroderivative gas turbines (with waste-heat recovery) mechanically drive the refrigerant compressors; 1xLM2500 aeroderivative turbine mechanically drives NGL-recovery booster compression; Solar Titan 130 aeroderivative gas turbine generators (with WHR) provide site power generation. | ~45-50 MW each for the 2xLM6000PF+ mechanical-drive units (LM6000 aeroderivative class rating per convention; no site-specific figure published); LM2500 booster-compression unit ~25-34 MW class; Solar Titan 130 power-generation units' rating not specified in source. | ~90-100 MW aggregate across the 2xLM6000PF+ mechanical-drive turbines (aeroderivative rule) | Aggregate >=50 MW (aeroderivative rule, mechanical drive) - 2xLM6000PF+ aeroderivative gas turbines mechanically driving refrigerant compressors aggregate to an estimated 90-100 MW at the standard LM6000 class rating; class inferred from the named turbine model, no site-specific figure published (JUDGMENT CALL - class-rating inference). | https://www.gastechevent.com/media/zoppuuti/damian-nguyen_wison-new-energies_2094.pdf, https://www.genting.com/wp-content/uploads/2024/10/GENT-Press-Release-on-Procurement-Contract-and-CIC-Contract-for-Genting-FLNG-project.pdf, https://klse.i3investor.com/web/blog/detail/ceomorningbrief/2024-10-29-story-h472823971-Genting_Commissions_Contractors_to_Build_Midstream_Infra_to_Link_Kasuri_
Dua FLNG Terminal | T100000130289 | Malaysia | operating | PFLNG DUA (moored offshore FLNG vessel): 4xGE PGT25+G4 aeroderivative gas turbine generator systems supply the facility's electric power; 2xLM6000-PF+ 2BCL907 aeroderivative gas turbines mechanically drive the nitrogen-liquefaction-train compressors. Both installed under GE Oil & Gas's November 2014 turbomachinery contract. | ~45-50 MW each for the 2xLM6000-PF+ mechanical-drive units (LM6000 aeroderivative class rating per convention; no site-specific figure published); PGT25+G4 power-generation units' individual rating not specified in source. | ~90-100 MW aggregate across the 2xLM6000-PF+ mechanical-drive turbines (aeroderivative rule); 4xPGT25+G4 power-generation turbines aggregate separately, MW not stated in source. | Aggregate >=50 MW (aeroderivative rule, mechanical drive) - 2xLM6000-PF+ aeroderivative turbines drive the nitrogen-train compressors at an estimated 90-100 MW aggregate (LM6000 class rating, JUDGMENT CALL - class-rating inference); separately confirms 4xPGT25+G4 aeroderivative generators for site power generation (MW not stated). | https://www.ge.com/news/press-releases/ge-oil-gas-supplying-malaysias-petronas-turbomachinery-second-floating-lng-facility, https://www.offshore-technology.com/projects/pflng-2-rotan-flng-project-sabah/
MLNG T9 LNG Terminal | T100000130293 | Malaysia | operating | 2xGE Frame 7EA heavy-duty gas turbines (mechanical drive), each paired with a 13 MW induction motor (VSI/VSD, 3,600 rpm) as a helper/assist unit, drive Train 9's LP/MP mixed-refrigerant and propane/HP mixed-refrigerant compression trains. The wider Bintulu Petronas LNG Complex also self-generates a portion of its electricity via on-site gas turbines. | ~85-90 MW shaft each (GE Frame 7EA class rating; no site-specific figure published) for the mechanical-drive turbines; the paired 13 MW motor is a helper/assist unit driving alongside, not a separate qualifying generator. | n/a (mechanical drive, heavy-duty individual-unit rule, not summed - combined class rating would be roughly 170-180 MW across both units) | Individual >=50 MW (mechanical drive; Frame 7EA class-rating inference, JUDGMENT CALL - class rating inferred from the named turbine model, no site-specific figure published). | https://www.ge.com/news/press-releases/petronas-selects-ge-technology-petronas-lng-train-9-project, https://www.offshore-energy.biz/malaysia-petronas-picks-ge-technology-for-lng-train-9-project/, https://www.petronas.com/flow/sustainability/sparking-sustainable-future-electrifying-petronas-lng-complex
Satu FLNG Terminal | T100000130288 | Malaysia | operating | PFLNG SATU (moored at the Kanowit field, off-grid by construction): 4x GE PGT25+G4 gas turbine generator sets supply on-site electricity, plus 2x PGT25+G4 gas turbines in mechanical-drive service on the liquefaction compression trains (alongside 2 electric-motor-driven compressor modules). | ~30-34 MW each (PGT25+G4 = industrial LM2500+G4; class rating, no site-specific figure published) | ~120-136 MW generator fleet (4 units); ~200 MW including the 2 mechanical-drive units (class-rating aggregate) | Aggregate >=50 MW (aeroderivative rule; PGT25+G4 is the industrial LM2500+G4 aeroderivative -- same class-inference basis as the Cameroon FLNG and Corpus Christi qualifiers). Individual units (~30-34 MW) are below threshold; the aggregate is the qualifying basis. | https://www.ge.com/news/press-releases/petronas-selects-ges-compressor-technology-asias-first-floating-lng-project-0
Tiga FLNG Terminal | T100000131063 | Malaysia | construction | Purpose-built onshore gas-fired power plant at Sipitang (Sabah), adjacent to PFLNG Tiga's nearshore mooring: 7xMAN Energy Solutions 20V35/44G gas engines, described by both the equipment vendor and independent trade press as becoming the sole electricity supply to the terminal. | 10 MW each (70 MW / 7 engines) - below the 50 MW individual threshold | 70 MW aggregate (7xMAN 20V35/44G gas engines) | Aggregate >=50 MW (genset rule) - 7 gas engines totaling 70 MW, explicitly the sole electricity supply to the terminal; well above the 50 MW aggregate threshold. | https://www.man-es.com/company/press-releases/press-details/2024/09/04/man-energy-solutions-to-supply-gas-engines-for-three-power-plants-in-southeast-asia, https://www.rivieramm.com/news-content-hub/news-content-hub/malaysia-gears-up-for-third-flng-project-82285, https://www.thestar.com.my/business/business-news/2024/04/01/petronas-begins-the-construction-of-its-third-floating-lng-facility

## Asia - Excluded
Terminal | Terminal ID | Country | Reason Excluded | MW Figure (if any) | References
Moheshkhali Floating LNG Terminal | T100000130270 | Bangladesh | No MW figure disclosed. Two boil-off-gas-fired boilers aboard FSRU Excellence supply the vessel's own electrical power for regasification pumps and other loads (confirmed by a July 2026 fire that damaged the boiler power/control cabling and forced a nationwide gas-supply cut); general FSRU-conversion literature suggests a 15-25 MW class range but no site-specific rating was found. | None disclosed (general FSRU literature suggests 15-25 MW class, not site-specific) | https://www.tbsnews.net/bangladesh/gas-crisis-deepens-lng-terminal-outage-disrupts-supply-cripples-household-cooking-1498596, https://thereport.live/bangladesh/gas-crisis-deepens-as-fsru-fire-disrupts-supply-relief-not-expected-soon/41055
Summit FSRU | T100000130272 | Bangladesh | Below the 50 MW threshold. 2x10 MW-class gas turbine generators (1 operating + 1 standby) supply the FSRU's captive power per the project EIA, which labels it a 'captive power generation facility'; only one unit runs at a time (10 MW), and even the full 2-unit nameplate (20 MW) does not clear the threshold. | 20 MW aggregate nameplate (2x10 MW-class gas turbine generators, 1 operating + 1 standby) | https://www.nexi.go.jp/environment/info/pdf/18-022_EIA_01.pdf
Hong Kong FSRU | T100000130388 | Hong Kong | Aggregate reported only as a floor value, not confirmed to clear 50 MW. 4xMAN 9L51/60 dual-fuel generators aboard the Bauhinia Spirit FSRU are each rated '>9 MW,' stated as '>36 MW aggregate' - a lower bound, not a precise figure, so it cannot be confirmed to reach the 50 MW threshold. | >36 MW aggregate (4xMAN 9L51/60 dual-fuel generators, each >9 MW; precise total not disclosed) - JUDGMENT CALL, treated as below threshold absent a confirmed figure | https://marine-offshore.bureauveritas.com/magazine/explore-mols-fsru-bauhinia-spirit-bureau-veritas
Chhara LNG Terminal | T100000130800 | India | Below the 50 MW threshold. An 18 MW gas-turbine-based captive power plant (CPP) is the terminal's primary power source per its Risk Assessment/EIA, with the Gujarat State grid as standby and an emergency diesel generator as further backup. | 18 MW (gas-turbine-based captive power plant) | https://environmentclearance.nic.in/writereaddata/online/RiskAssessment/030120170Q1QDMZ8RiskAssessment.pdf
Dahej LNG Terminal | T100000130427 | India | Below the 50 MW threshold based on the only figure available. Three GTG packages form Petronet's on-site captive power plant per an EPC technical specification (no MW stated there); media reporting (not independently verified this pass) puts existing capacity at roughly 25 MW aggregate - well under the threshold either way. | ~25 MW aggregate (media estimate, not independently verified this pass; the primary EPC technical spec does not itself state an MW figure) | https://pdfcoffee.com/a324-00-tg-sp-0030-pdf-free.html, https://www.adb.org/sites/default/files/project-documents/39921-ind-siee.pdf
Dhamra LNG Terminal | T100000130431 | India | Below the 50 MW threshold. Three 9.6 MW gensets (29 MW total) based on 20-cylinder Rolls-Royce Bergen B35:40 gas engines, delivered as a full EPC gas power plant to meet the terminal's baseload power requirement. | 29 MW aggregate (3x9.6 MW gensets) | https://www.rolls-royce.com/media/press-releases/2020/06-10-2020-rr-to-deliver-29-mw-gas-power-plant-for-dhamra-lng-regasification-terminal-in-india.aspx, https://www.dtnext.in/news/business/rollsroyce-to-deliver-29-mw-gas-power-plant-for-dhamra-lng-terminal, https://www.cnbctv18.com/energy/rolls-royce-to-deliver-29-mw-gas-power-plant-to-dhamra-lng-terminal-7118821.htm
Ennore LNG Terminal | T100000130662 | India | Below the 50 MW threshold. On-site captive combined-heat-and-power plant using gas turbine generators, rated 27 MW by the EPC contractor (Black & Veatch) or 26 MW per IndianOil LNG's own post-expansion power-balance filing (14 MW existing + 12 MW for the 5->10 MMTPA expansion). | 26-27 MW (captive CHP gas turbine plant; EPC contractor figure vs. operator filing) | http://indianoillng.com/wp-content/uploads/2026/07/IOLPL-Expansion-EC-CRZ-Clearance.pdf, https://www.bv.com/projects/ennore-lng-terminal-black-and-veatch-completes-design-to-commissioning-of
Gopalpur LNG Terminal | T100000131145 | India | No MW figure disclosed. GTGs for captive power are named as a Phase-II land-based-terminal design element (item 25 of 26) in Petronet's MoEFCC Terms of Reference for the proposed terminal; model, count, and MW rating are not stated. Current Phase-I power needs are grid-fed from the Chhatrapur substation, separate from this Phase-II design element. | None disclosed | https://parivesh.nic.in/certificates/PETRONET_LNG_LIMITED_(PLL)/5/4312635/specific_tor_IA_OR_INFRA1_424189_2023_4312636_-signed.pdf
Jafrabad FSRU | T100000130457 | India | Below the 50 MW threshold. 4xWartsila-Hyundai W9L50DF dual-fuel DFDE generator sets, 8,775 kW each (35.1 MW total), aboard the assigned FSRU vessel (Vasant 1) supply the vessel's hotel load, propulsion, and the regasification process. | 35.1 MW aggregate (4x8,775 kW dual-fuel DFDE gensets) | https://eplan.irclass.org:8090/IRS_Ship_Info.aspx?Imo_no=9837066
Jaigarh LNG Terminal | T100000130443 | India | Below the 50 MW threshold. 4xWartsila-Hyundai dual-fuel DFDE generator sets (1x6L50DF + 3x8L50DF) totaling 28,500 kW aboard the Phase-I FSRU (Hoegh Giant), supplying propulsion, hotel load and the regasification train while moored. | 28.5 MW aggregate (4 dual-fuel DFDE gensets) | https://www.ship-db.de/nawbn.php?wbn_nr=HYHU2552010E
Kochi LNG Terminal | T100000130447 | India | Below the 50 MW threshold. A 13 MW on-site captive gas turbine generator (GTG) plant supplies part of the terminal's power, topped up by Kerala State Electricity Board grid import; a separate 1.6 MVA diesel emergency DG set is backup-only and non-gas. | 13 MW (captive gas turbine generator plant; partial supply alongside grid) | https://environmentclearance.nic.in/auth/FORM_A_PDF.aspx?cat_id=IA/KL/IND2/229000/2021, https://petronetlng.in/documents/d/pertonetlng/nit_39?download=true
Bontang LNG Terminal | T100000130278 | Indonesia | No MW figure disclosed for the primary on-site mechanical-drive system (gas-fired boilers driving a steam turbine that runs the refrigerant compressor); a separately documented 13.4 MW gas turbine at the plant (per its own 1998 equipment data book) falls below the 50 MW threshold on its own. Terminal-level status is mixed (retired/idled/cancelled recorded among unit-level statuses in GEM data, but the mechanical-drive system remains operating/active, so this is not a status-gate exclusion). | 13.4 MW documented gas turbine (below threshold on its own); no MW figure disclosed for the primary boiler/steam-turbine mechanical-drive system | https://www.dunia-energi.com/collaborating-with-pln-badak-lng-encourages-innovation-to-increases-efficiency/, https://api.crossref.org/works/10.1063/5.0073900
Lampung FSRU | T100000130283 | Indonesia | No vessel-specific MW figure disclosed. PGN FSRU Lampung is managed by Hoegh LNG Fleet Management and described only via a fleet-wide company statement that Hoegh's FSRUs use dual-fuel diesel-electric (DFDE) generator sets; a sister vessel's rating (Hoegh Esperanza, 4x7,800 kW = 31.2 MW) is explicitly NOT attributed to this hull in the source. | None disclosed for this vessel (sister-vessel reference of 31.2 MW aggregate explicitly not attributed to Lampung) | https://www.rivieramm.com/news-content-hub/hoegh-lng-takes-delivery-of-its-ninth-fsru-22463, https://directory.marinelink.com/ships/ship/pgn-fsru-lampung-5559
Tangguh LNG Terminal | T100000130286 | Indonesia | No MW figure disclosed for the on-site captive system. Heavy-duty gas turbines mechanically drive the LNG-train refrigeration compressors, and their waste heat is recovered via HRSG to generate electricity used internally, with a small surplus (4 MW) historically sold to PLN; exact turbine model/count and total generating MW are not disclosed in sources found. | None disclosed (only ancillary figure found is 4 MW historically sold to PLN, not the total on-site captive capacity) | https://www.adb.org/sites/default/files/project-documents//49222-001-esia-03.pdf, https://turbomachinerymag.com/view/baker-hughes-signs-parts-repair-engineering-contract-for-tangguh-lng
Tanjung Benoa FSRU | T100000130276 | Indonesia | No MW figure disclosed. The FSRU Karunia Dewata carries a dual-fuel (DFDE-type) auxiliary generator set with a SOGAV gas-admission fuel system, confirmed gas-fired by a 2025 maritime-academy thesis documenting a 2022 fault incident, but no nameplate rating is published. | None disclosed | http://eprints.pipmakassar.ac.id/1239/
Hatsukaichi LNG Terminal | T100000130473 | Japan | Below the 50 MW threshold. 2xMHIET KU30GA natural gas engines, 5,500 kW each (11 MW total), gas-engine cogeneration installed 2004 (retrofitted 2018) to power the terminal's own refrigeration/vaporization load, with surplus power wheeled to the grid. | 11 MW aggregate (2x5,500 kW gas-engine cogeneration units) | https://www.hiroshima-gas.co.jp/com/w_new/new03_11/hatsu_c.htm, https://www.mhi.com/jp/group/mhiet/news/20181128.html
Naoetsu LNG Terminal | T100000130505 | Japan | No MW figure disclosed. On-site gas turbine generator is one of two non-normal/emergency power sources (the other diesel) backing up the dual utility grid feed at INPEX's Naoetsu terminal (standby_backup category); count, model and MW are not published. | None disclosed (standby/emergency-duty gas turbine generator; count and model undisclosed) | https://www.tmeic.co.jp/column/p2_vol03/
Yokkaichi Works LNG Terminal | T100000130533 | Japan | Below the 50 MW threshold. 3x5,500 kW gas-engine cogeneration units (16.5 MW total) at Toho Gas's own Yokkaichi Works, commissioned Oct 2017 explicitly for internal power-demand balancing, with waste heat feeding on-site city-gas manufacturing. | 16.5 MW aggregate (3x5,500 kW gas-engine cogeneration units) | https://www.tohogas.co.jp/corporate-n/press/1205024_1342.html, https://www.nikkan.co.jp/articles/view/444977
Yoshinoura LNG Terminal | T100000130837 | Japan | Below the 50 MW threshold. The 35,000 kW (35 MW) Yoshinoura Multi-Gas-Turbine plant (LNG-primary multi-fuel) provides island blackstart, LNG-tank security backup, peak-demand response, and BOG-processing duty for the terminal, but total plant capacity is 35 MW. | 35 MW (Yoshinoura Multi-Gas-Turbine plant total) | https://ja.wikipedia.org/wiki/%E5%90%89%E3%81%AE%E6%B5%A6%E7%81%AB%E5%8A%9B%E7%99%BA%E9%9B%BB%E6%89%80, https://release.itmedia.co.jp/release/sj/2015/03/20/3d55355e70e6ae850423a801da9c05e6.html
MLNG Dua LNG Terminal | T100000130292 | Malaysia | No MW figure disclosed at the individual-terminal/train level. Complex-wide, Petronas states the Bintulu complex relied 'solely on gas-powered turbines' before a 2024 grid tie-in (Project GLORY) substituted 40%/90 MW of total demand with Sarawak hydro, leaving the majority still gas-turbine-generated jointly across MLNG, MLNG Dua and MLNG Tiga - not apportioned to this terminal specifically. JUDGMENT CALL: complex-level context is suggestive but not documented per train. | None disclosed at the individual-terminal level (complex-wide majority of >~135 MW implied gas-turbine demand shared across 3 terminals, per the Project GLORY 90 MW/40% substitution figure) | https://www.petronas.com/flow/sustainability/sparking-sustainable-future-electrifying-petronas-lng-complex, https://www.ge.com/news/press-releases/ge-wins-1276-million-service-contract-malaysia-lng-complex, https://lngprime.com/lng-terminals/sarawak-energy-to-power-petronas-bintulu-lng-complex/13808/
MLNG Satu LNG Terminal | T100000130294 | Malaysia | No MW figure disclosed at the individual-terminal/train level. Complex-wide, Petronas states the Bintulu complex relied 'solely on gas-powered turbines' before a 2024 grid tie-in (Project GLORY) substituted 40%/90 MW of total demand with Sarawak hydro, leaving the majority still gas-turbine-generated jointly across MLNG, MLNG Dua and MLNG Tiga - not apportioned to this terminal specifically. JUDGMENT CALL: complex-level context is suggestive but not documented per train. | None disclosed at the individual-terminal level (complex-wide majority of >~135 MW implied gas-turbine demand shared across 3 terminals, per the Project GLORY 90 MW/40% substitution figure) | https://www.petronas.com/flow/sustainability/sparking-sustainable-future-electrifying-petronas-lng-complex, https://www.ge.com/news/press-releases/ge-wins-1276-million-service-contract-malaysia-lng-complex, https://lngprime.com/lng-terminals/sarawak-energy-to-power-petronas-bintulu-lng-complex/13808/
MLNG Tiga LNG Terminal | T100000130295 | Malaysia | No MW figure disclosed at the individual-terminal/train level. A GE long-term service agreement names MLNG, MLNG Dua and MLNG Tiga jointly as covering 'the power generation units and liquefaction trains' for the complex; Petronas' own electrification account confirms the wider complex traditionally self-generated its power via on-site gas turbines (now ~40%/90 MW substituted by Sarawak grid hydro), but no MW figure is apportioned to this terminal specifically. JUDGMENT CALL: complex-level context is suggestive but not documented per train. | None disclosed at the individual-terminal level (complex-wide majority of >~135 MW implied gas-turbine demand shared across 3 terminals, per the Project GLORY 90 MW/40% substitution figure) | https://www.ge.com/news/press-releases/ge-wins-1276-million-service-contract-malaysia-lng-complex, https://www.petronas.com/flow/sustainability/sparking-sustainable-future-electrifying-petronas-lng-complex

## ME-Gulf - Qualifying (>=50MW)
Terminal | Terminal ID | Country | Status | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | References
Iran NIOC LNG Terminal | T100000130583 | Iran | construction (LNG trains suspended by client since mid-2013 under sanctions); dedicated power plant completed and grid-connected unit-by-unit since ~2022 | Dedicated on-site CCGT power station purpose-built for the Iran LNG project's own use (project Package I-C, 'E-LNG': Power Station, Electric Motors and Compressors), comprising 5 gas turbine units and 2 steam turbine units, aggregate 1,130 MW nameplate. Also carries 4 dedicated 3.3 MVA diesel gensets for emergency backup (diesel-only, not counted toward the fuel gate). | 162 MW each (5 gas turbine units) and 160 MW each (2 steam turbine units), per project design table | 1,130 MW aggregate nameplate (not required to qualify; individual units already clear threshold) | Individual >=50 MW (heavy-duty CCGT units, 162 MW/160 MW each). As-designed captive power counts per SOP even though the LNG trains themselves never started up and the completed power units have since been connected to Iran's national grid. | https://www.ogj.com/exploration-development/reserves/article/17228246/iran-details-lng-liquefaction-plans, https://www.power-technology.com/data-insights/power-plant-profile-iran-lng-combined-cycle-power-plant-iran/, https://mapnagroup.com/1232/%D8%A7%D8%AA%D8%B5%D8%A7%D9%84-%D9%88%D8%A7%D8%AD%D8%AF-%D9%BE%D9%86%D8%AC%D9%85-%DA%AF%D8%A7%D8%B2%DB%8C-%D9%86%DB%8C%D8%B1%D9%88%DA%AF%D8%A7%D9%87-%D8%A7%DB%8C%D8%B1%D8%A7%D9%86-%D8%A7%D9%84-%D8%A7/
Oman Qalhat LNG Terminal | T100000130593 | Oman | operating (power-generation plant and mechanical-drive compression trains); proposed (per GEM status list) | Mixed site. (1) On-site power-generation plant: originally 4x GE Frame 6 gas turbine-generators (120 MW total), replaced circa 2018-2020 by nine MAN 51/60 reciprocating gas engines rated 120 MW total, supplying electricity to the LNG facility. (2) Separate mechanical-drive gas turbines run the compressor trains: a 280 MW GE Frame 7 gas turbine drives the mixed-refrigerant compression train and a 42 MW GE Frame 6 gas turbine drives the propane compression train (Train 3/debottlenecking expansion). | 280 MW (GE Frame 7, mechanical drive, MR train) qualifies individually; 42 MW (GE Frame 6, mechanical drive, propane train) is below the individual threshold; MAN gas-engine units are ~13 MW each (120 MW / 9 units), below the individual threshold | 120 MW aggregate for the on-site MAN gas-engine power plant (genset rule applies to reciprocating gas engines) qualifies on its own | Qualifies both ways: Individual >=50 MW (mechanical drive, 280 MW GE Frame 7) AND Aggregate >=50 MW (genset rule, 120 MW MAN gas-engine power plant, both the legacy Frame 6 and current MAN configurations). | https://www.ge.com/news/press-releases/ge-oil-and-gas-signs-us94-million-contract-oman-lng-project-ge-supply-gas-turbines, https://www.lngindustry.com/liquid-natural-gas/13072018/man-to-power-gas-engine-power-plant-in-oman/
QatarEnergy LNG (N) | T100000130594 | Qatar | operating | Heavy-frame gas turbines mechanically shaft-drive the refrigeration compressor strings across this entity's Ras Laffan trains (Qatargas-heritage side): GE Frame 9E turbines (~132 MW ISO rating, documented) on the Qatargas II mega-trains via a Siemens VFD/Ansaldo motor-generator system that can also export surplus electrical power to the plant grid; GE Frame 5C/5D turbines on the earlier trains drive the mixed-refrigerant and propane refrigeration cycles. | ~132 MW ISO each (GE Frame 9E, documented rating in source) qualifies individually; Frame 5C/5D units have no site-specific figure published (class rating ~25-32 MW, below threshold if inferred) | n/a (mechanical drive, heavy-duty single units, not summed) | Individual >=50 MW (mechanical drive, GE Frame 9E ~132 MW ISO documented rating on the Qatargas II mega-trains). | https://www.ogj.com/general-interest/companies/article/17228343/worlds-largest-lng-compressors-designed-tested-for-qatargas-ii, https://www.ogj.com/general-interest/companies/article/17231479/qatargas-upgrades-debottlenecks-ras-laffan-lng-plant, https://www.bakerhughes.com/sites/bakerhughes/files/2021-02/BakerHughes_Frame91E_Overview-012921.pdf, https://pdfcoffee.com/start-up-and-operation-of-ge-frame-9e--pdf-free.html
QatarEnergy LNG (S) | T100000130598 | Qatar | operating | Heavy-frame gas turbines mechanically shaft-drive the refrigeration compressor strings on this entity's Ras Laffan trains (RasGas-heritage side): two GE Frame 7EA turbines (DLN-retrofitted 2011) drive the mixed-refrigerant and propane compressor trains on the earlier trains, and GE Frame 9E turbines (~132 MW ISO class) drive the Train 6-7 mega-trains, described by the turbine vendor as 'the world's largest mechanical-drive application.' | ~132 MW ISO each (GE Frame 9E, documented rating in source) qualifies individually; ~85-90 MW each (GE Frame 7EA; Frame 7 class rating inference, no site-specific figure published) also qualifies individually | n/a (mechanical drive, heavy-duty single units, not summed) | Individual >=50 MW (mechanical drive; Frame 9E ~132 MW ISO documented + Frame 7EA ~85-90 MW class-rating inference, both named turbine models). | https://www.bakerhughes.com/sites/bakerhughes/files/2021-02/BakerHughes_Frame91E_Overview-012921.pdf, https://pdfcoffee.com/start-up-and-operation-of-ge-frame-9e--pdf-free.html

## ME-Gulf - Excluded
Terminal | Terminal ID | Country | Reason Excluded | MW Figure (if any) | References
South Pars LNG Terminal | T100000130916 | Iran | Cancelled - excluded per instruction. Published project design (OGJ 2010) included a dedicated 1,000 MW combined-cycle gas turbine power plant built specifically 'to provide power for the project'; turbine count/model not disclosed in the source found - would qualify if active. | 1,000 MW aggregate CCGT plant (project cancelled; Total withdrew 2008, project presumed cancelled) | https://www.ogj.com/pipelines-transportation/lng/article/17209101/ogj-focus-iranian-lng-natural-gas-export-plans-outlined
Khor Al-Zubair FSRU | T100001048168 | Iraq | No MW figure disclosed. Dual-fuel diesel-electric (DFDE) generating engines aboard the assigned FSRU (Excelerate Acadia, Hull 3407, 170,000 m3) supply the vessel's own onboard electric power for storage/regasification/hotel loads, but no engine model or MW rating is publicly disclosed. Status is proposed. | None disclosed (FSRU onboard DFDE gensets, no MW rating published) | https://www.lngindustry.com/floating-lng/08072025/excelerate-energy-launches-fsru-in-south-korea/, https://bunkerindex.com/articles/article.php?a=22645&h=bureau-veritas-classifies-excelerate-energys-new-170000-cbm-fsru-excelerate-acadia, https://www.tradewindsnews.com/gas/excelerate-energy-allocates-its-lone-fsru-newbuilding-to-iraq/2-1-1892466, https://excelerateenergy.com/news/excelerate-energy-signs-definitive-agreement-for-fully-integrated-floating-lng-import-terminal-in-iraq/
Aqaba Jordan FSRU | T100000130591 | Jordan | No MW figure disclosed. The assigned FSRU (Energos Eskimo, ex-Golar Eskimo) self-generates 100% of its own onboard power via a Wärtsilä DFDE (dual-fuel diesel-electric) plant, but engine count/MW is not publicly disclosed. Terminal is currently idled. | None disclosed (FSRU onboard DFDE gensets) | https://www.golarlng.com/~/media/Files/G/Golar-Lng/sustainability/Golar%20fleet%20-%202019%20Key%20facts%20and%20figures%20150720.pdf, https://energosinfra.com/fleet-assets/
Mina Al-Ahmadi LNG Terminal | T100000130592 | Kuwait | No MW figure disclosed. Both FSRUs assigned to this terminal (Explorer, now idled; Golar Igloo, now mothballed) self-generate power via onboard dual-fuel diesel-electric (DFDE) gensets - Wärtsilä 50DF engines are used on 14 of 16 fleet vessels - but no vessel-specific nameplate MW figure was found for either unit. | None disclosed (FSRU onboard DFDE gensets); terminal status idled/mothballed | https://www.offshore-energy.biz/spotted-upgraded-explorer-ups-the-ante/, https://gcaptain.com/wartsila-reaches-major-milestone/, https://www.offshore-mag.com/vessels/article/14196056/golar-prolongs-wartsila-fsru-maintenance-arrangement
Das Island LNG Terminal | T100000130601 | United Arab Emirates | Below threshold. On-site power generation comprises 5x legacy GE Frame 5 gas turbine-generators (no site-specific total; Frame 5 class rating ~25-32 MW each) plus a newer, explicitly-rated 36 MW GE Frame 6 power station (commissioned ~2015); mechanical-drive compression uses 2x GE Frame 5D turbines (~25-32 MW class rating). No individual heavy-duty unit reaches the 50 MW threshold, and heavy-duty single-turbine fleets are judged individually, not aggregated. | 36 MW (newer GE Frame 6 power station, explicit figure); GE Frame 5 / Frame 5D units estimated ~25-32 MW each (class rating, no site-specific figure) - all below 50 MW individually | https://www.oilandgasonline.com/doc/ge-oil-gas-to-supply-turbocompressors-to-adga-0001, https://www.ge.com/news/press-releases/ge-oil-gas-supply-turbocompressors-adgas-das-island-lng-complex-0, https://www.setec.fr/en/blog/projets/das-island-thermal-power-station/
Yemen LNG Terminal | T100000130605 | Yemen | No MW figure disclosed. Both Balhaf liquefaction trains are compressor-driven by heavy-duty gas turbines in a 1x100% shaftline arrangement (industry-standard mechanical drive), but no turbine model/frame class is named in the source, precluding a class-rating inference. GE-supplied 11 MW induction motors (4 total) are starter/helper units only, not the prime mover, and do not themselves qualify. Terminal has been mothballed since 2015 (as-built design finding persists regardless of current idle status). | None disclosed (turbine model/frame not named); 11 MW induction motors are starter/helper only, not prime movers | https://www.gasprocessingnews.com/articles/2021/10/turbomachinery-configuration-for-lng-project-concept-selection/, https://www.gevernova.com/power-conversion/case-study/electrical-solution-with-induction-motors-for-lng-yemen

## Africa - Qualifying (>=50MW)
Terminal | Terminal ID | Country | Status | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | References
Skikda LNG Terminal | T100000130244 | Algeria | operating (GL1K/Skikda complex); retired (GL4Z, not the qualifying unit) | GL1K/Skikda complex runs on-site GE gas turbines in liquefaction mechanical-drive service: a GE MS5002D (Frame 5-class) unit and a GE MS7001EA/DLN-1 (Frame 7EA-class) unit, confirmed by Sonatrach's own rotor-overhaul procurement tenders. | ~85-90 MW shaft (GE MS7001EA/DLN-1, Frame 7EA class rating; no site-specific figure published); the MS5002D (Frame 5 class, ~25-32 MW) does not independently qualify | n/a (mechanical drive, not summed) | Individual >=50 MW (mechanical drive, via the Frame 7EA-class MS7001EA unit; Frame-class inference from named model) | https://rhinotenders.com/tenders/tender/acquisition-d-un-rotor-complet-hp-bp-pour-turbine-a-gaz-ge-ms5002d-zasqr, https://rhinotenders.com/tenders/tender/acquisition-d-un-rotor-complet-pour-la-turbine-a-gaz-de-marque-ge-ms7001e-kyngk
Cameroon FLNG Terminal | T100000130247 | Cameroon | operating | GE PGT25+G4 DLE aeroderivative (LM2500-derived) gas turbines mechanically driving GE 2BCL refrigeration compressors across four PRICO liquefaction trains on Hilli Episeyo, plus two dedicated Rolls-Royce Bergen B35:40V20AG dual-fuel reciprocating gensets for the vessel's own power generation. | ~25-34 MW each (LM2500-derived aeroderivative class inference from the hardware description's own 'LM2500-derived' label; no site-specific per-unit figure published); Bergen genset rating not disclosed | ~100-136 MW aggregate across the four PGT25+G4 trains (aeroderivative rule, class-inferred, not a published site figure) | Aggregate >=50 MW (aeroderivative rule; class rating inferred only from the source's own 'LM2500-derived' description, not a site-specific figure) — JUDGMENT CALL, flag for review | https://www.offshore-energy.biz/ge-tech-ordered-for-hilli-flng-conversion/, https://gcaptain.com/rolls-royce-power-golars-new-floating-lng-liquefaction-ship/, https://www.offshore-energy.biz/rolls-royce-engines-for-golar-flngv/
Damietta SEGAS LNG Terminal | T100000130249 | Egypt | operating (T1); shelved (T2, same design, never built) | Two GE Frame 7 (7EA) gas turbines shaft-drive the Split MRTM propane/mixed-refrigerant compressor trains on operating Train 1 - one drives the propane and HP MR compressors, the other the LP/MP MR compressors; no electricity generated by these units. | ~85-90 MW shaft each (Frame 7EA class rating; no site-specific figure published) | n/a (mechanical drive, not summed) | Individual >=50 MW (mechanical drive, Frame 7EA class inference from named model) | https://www.gpaeurope.com/sites/default/files/download-file/documents/conference-papers/paper-6-MWK-LNG14-Segas.pdf
Marsa El Brega LNG Terminal | T100000130255 | Libya | MOTHBALLED (entire terminal) - MW test applied per instruction, not silently decided | Three open-cycle gas turbine generating units at the co-located Sirte Oil Co. power plant (same 100% owner GEM records for the LNG terminal, coordinates within ~1 km of the terminal), commissioned 1977, dedicated on-site electricity generation. | ~20.7 MW each (62 MWe combined design capacity divided by 3 units; no per-unit figure published) | 62 MWe combined design capacity (single-source: Global Energy Observatory) | Aggregate >=50 MW (genset/generating-fleet rule, explicit combined figure); terminal status is MOTHBALLED, and underlying source confidence is single-source (yellow) - JUDGMENT CALL applying the aggregate rule to unnamed open-cycle GT generating units rather than a named heavy-duty individual unit, flag for review | http://globalenergyobservatory.org/geoid/41593
Mozambique LNG Terminal | T100000130257 | Mozambique | construction (project restarted 2026 per TotalEnergies/gascompressionmagazine); shelved reflects a prior suspended phase, not current cancellation | Six Siemens Energy SGT-800 industrial gas turbine generators (54 MW each, 39% gross efficiency, dry low-emission combustion) dedicated to on-site power generation, plus four Siemens Energy centrifugal compressors for boil-off-gas service. | 54 MW each (Siemens Energy SGT-800 nameplate, explicitly stated - not inferred) | ~324 MW aggregate (6 x 54 MW) | Individual >=50 MW (power generation; explicit nameplate figure, not inferred) | https://www.offshore-energy.biz/siemens-gets-mozambique-lng-turbines-job/, https://gascompressionmagazine.com/2026/01/31/totalenergies-restarts-mozambique-lng-project/
Rovuma LNG Terminal | T100000130789 | Mozambique | proposed | Mitsubishi Heavy Industries H-100 dual-shaft 120 MW gas turbines as mechanical drivers for the main liquefaction (refrigeration) compressors, Phase 1 (two trains, Air Products AP-X process). | 120 MW each (explicit MHI nameplate figure, not inferred) | n/a (mechanical drive, not summed) | Individual >=50 MW (mechanical drive; explicit nameplate figure) | https://www.offshore-energy.biz/mitsubishi-heavy-to-supply-equipment-for-rovuma-lng-project/
Nigeria LNG Terminal | T100000130259 | Nigeria | operating (Trains 1-6); construction (Train 7 expansion); shelved/proposed reflect other historic or future trains, not the operating core | Ten gas-turbine generators dedicated to on-site power generation (combined >320 MW) at the six-train Bonny Island complex, plus four heavy-duty gas turbines mechanically driving the liquefaction refrigeration compressors; the Train 7 expansion adds three more generator turbines. | n/a - individual per-unit MW not disclosed for the 10-turbine generation fleet | >320 MW aggregate (10 gas turbine generators; explicit combined figure per NS Energy Business/GlobalData) | Aggregate >=50 MW (genset/generating-fleet rule; explicit combined figure, not inferred) | https://www.bakerhughes.com/company/news/baker-hughes-extends-longterm-service-agreement-nigeria-lng-support-critical-expansion, https://www.nsenergybusiness.com/projects/nigeria-lng-plant-expansion-bonny-island/

## Africa - Excluded
Terminal | Terminal ID | Country | Reason Excluded | MW Figure (if any) | References
Arzew-Bethioua LNG Terminal | T100000130243 | Algeria | No MW figure disclosed. Mechanical-drive gas turbines confirmed at the GL3Z liquefaction train via Sonatrach's own gas-turbine-air-filter procurement tender, but no turbine model or MW rating is disclosed in the tender; GL1Z's separately-run GE steam turbines are waste-heat/process-steam units, not gas-fired power. | None disclosed (mechanical drive) | https://file05.erui.com/group1/M00/00/BF/rBFIw2Rut5yAEweyAAPfogTObfs042.pdf
Angola LNG Terminal | T100000130245 | Angola | No MW figure disclosed. Two GE gas-turbine-driven compression trains confirmed at the Soyo liquefaction plant under a 2012 GE service agreement (corroborated by GE's own press release and an independent trade-press article), but no turbine model or MW rating is disclosed in either source. | None disclosed (mechanical drive) | https://www.ge.com/news/press-releases/angola-lng-plant-ensuring-gas-supply-through-ge-service-agreement, https://www.offshore-energy.biz/angola-lng-contract-goes-to-ge/
Ain Sokhna FSRU | T100000130685 | Egypt | No MW figure disclosed. Sole currently-operating unit Energos Power runs MAN TFDE tri-fuel diesel-electric generating machinery (gas-capable), per the operator's own fleet page - fleet-level FSRU-onboard generator evidence only, no MW rating published. | None disclosed | https://energosinfra.com/our_fleet/energos-power/
Damietta FSRU | T100001083032 | Egypt | No MW figure disclosed. Sole unit Energos Winter runs steam-turbine machinery with dual-fuel boilers (vessel-class convention, gas-capable) feeding turbo-generators for the vessel's own power; no MW rating published, and the gas-burning capability rests on class convention rather than a vessel-specific statement. | None disclosed | https://energosinfra.com/our_fleet/energos-winter/, https://en.wikipedia.org/wiki/LNG_carrier
Egyptian LNG Terminal | T100000130250 | Egypt | 12x GE Frame 5-2D (MS5002D) gas turbines drive the plant's 20 refrigeration compressors across two trains. Frame 5-class heavy-duty industrial turbines are individually rated ~25-32 MW (class inference from the named model), below the 50 MW threshold; heavy-duty single units are judged individually, not aggregated. A separate shared electric 'power generation unit' utility is documented but its fuel is not stated. | ~25-32 MW each (GE Frame 5-2D/MS5002D class rating); 12 units, all below threshold individually | https://www.oilandgasonline.com/doc/agreement-covers-12-gas-turbines-20-compresso-0001, https://egyptoil-gas.com/news/egyptian-lng-upgrade-project-to-mark-debut-of-ges-power-crystal-technology/, https://www.nsenergybusiness.com/projects/egyptian-lng-project-idku/
Sumed FSRU | T100000130686 | Egypt | No MW figure disclosed. GEM-listed operating unit Energos Eskimo runs Wärtsilä DFDE dual-fuel diesel-electric generating machinery (gas-capable), per the operator's own fleet page - fleet-level FSRU-onboard generator evidence only, no MW rating published. | None disclosed | https://energosinfra.com/our_fleet/energos-eskimo/, https://squadronenergy.com/wp-content/uploads/pdf/Port-Kembla-Energy-Terminal/PDF/Environmental-Impact-Statement/Appendix-M-Air-quality.pdf
Greater Tortue Ahmeyim FLNG Terminal | T100000130661 | Mauritania | No MW figure disclosed. Two Rolls-Royce Bergen B35:40V20AG dual-fuel reciprocating gensets confirmed for the Gimi FLNG vessel's own power generation (design shared with, and confirmed built on, sister vessel Hilli; contractually optioned for Gimi by name in the same 2015 contract), but no MW rating is stated in the source, and the as-built Gimi configuration is not independently confirmed post-conversion. | None disclosed | https://gcaptain.com/rolls-royce-power-golars-new-floating-lng-liquefaction-ship/, https://lngprime.com/africa/golar-says-gimi-flng-86-percent-complete/59169/, https://www.golarlng.com/fleet.aspx
Coral North FLNG Terminal | T100000131124 | Mozambique | No MW figure disclosed. As-designed replica of Coral Sul FLNG's topsides (aeroderivative-gas-turbine-driven mechanical-drive compression plus separate turbo-generation units), but the vendor/turbine model has not yet been separately announced for this hull, and the project is still proposed/pre-startup (targeted 2028). | None disclosed (design not yet equipment-specific) | https://www.offshore-energy.biz/mozambiques-second-flng-project-on-technipfmcs-to-do-list/, https://www.offshore-energy.biz/eni-cheers-launch-of-its-mozambique-bound-flng-at-samsung-heavy-industries-shipyard/
Coral South FLNG Terminal | T100000130258 | Mozambique | No MW figure disclosed. Four aeroderivative-gas-turbine turbo-compression trains (mechanical drive) plus four aeroderivative-gas-turbine turbo-generation units (GE Power Conversion generators) are confirmed by two independent Baker Hughes contract-win articles, but neither names a specific turbine model or MW rating, so no class-rating inference is possible. | None disclosed (no turbine model named) | https://www.offshore-energy.biz/baker-hughes-in-another-coral-south-win/, https://www.offshore-energy.biz/baker-hughes-secures-another-coral-south-flng-contract/
Eni Congo FLNG II Terminal | T100000131123 | Republic of the Congo | No MW figure disclosed. Dual-fuel main generator plus waste-heat-recovery units are confirmed by two independent publishers to supply the moored Nguya FLNG's own power/hotel load (no shore grid connection), but no model, unit count, or MW rating is disclosed in either source. | None disclosed | https://www.offshore-energy.biz/new-unit-ready-to-complete-flng-pair-at-enis-congolese-project/, https://www.bairdmaritime.com/offshore/vessels-rigs-fposfpsos/vessel-review-nguya-floating-liquefaction-unit-to-support-enis-lng-project-off-congo

## Oceania - Qualifying (>=50MW)
Terminal | Terminal ID | Country | Status | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | References
Australia Pacific LNG Terminal | T100000130327 | Australia | operating | Seven Bechtel-installed gas turbine generators (~15 MW each) supplying the electrical power for the two Curtis Island LNG processing trains; unit sizing (~15 MW each) is consistent with a small/genset-class turbine rather than a heavy-duty industrial frame unit. | ~15 MW per unit (below 50 MW threshold individually) | ~105 MW combined (7 x ~15 MW) | Aggregate >=50 MW (genset/small-turbine rule) -- JUDGMENT CALL: turbine model is not named in the source; aggregate treatment is inferred from unit size (~15 MW, below any heavy-duty frame class) rather than a documented aeroderivative label. Flag for review. | https://www.lngindustry.com/liquefaction/22042015/aplng-starts-first-gas-generator-629/
Gladstone LNG Terminal | T100000130333 | Australia | operating | Six gas turbine generators on Curtis Island (~12 MW each) providing the plant's permanent electrical power supply, running compressors, pumps, and other heavy electrical equipment; unit sizing (~12 MW each) is consistent with a small/genset-class turbine rather than a heavy-duty industrial frame unit. | ~12 MW per unit (below 50 MW threshold individually) | ~72 MW combined (6 x ~12 MW) | Aggregate >=50 MW (genset/small-turbine rule) -- JUDGMENT CALL: same reasoning as Australia Pacific LNG (model not named, aggregate inferred from small unit size). Flag for review. | https://www.lngindustry.com/liquid-natural-gas/10042015/santos-starts-up-generators-on-curtis-island-571/
Gorgon LNG Terminal | T100000130334 | Australia | operating; cancelled (unspecified expansion/component only -- the terminal-level facility remains active and operating, so it is not excluded on status) | Five on-site gas turbine generators on Barrow Island generating up to 584 MW combined at full output, powering the Gorgon LNG/domestic-gas processing complex -- Chevron Australia's managing director described the output as comparable in scale to the Kwinana power station supplying greater Perth, consistent with heavy-duty industrial frame-class turbines. | ~117 MW per unit (computed: 584 MW / 5 units), consistent with heavy-duty frame-class turbine territory | 584 MW combined at full output | Qualifies both ways: individual >=50 MW (heavy-duty single units, ~117 MW each) and aggregate >=50 MW (584 MW total). No material judgment call -- both figures clear the threshold comfortably. | https://thewest.com.au/news/wa/chevron-celebrates-turbine-start-up-ng-ya-388775
Wheatstone LNG Terminal | T100000130344 | Australia | operating | 12x GE LM6000PF aero-derivative gas turbines (6 per LNG train, 2 trains) in pure mechanical-drive service, directly shaft-driving the ConocoPhillips Optimized Cascade refrigeration compressors with no electricity generated -- the first industrial application of the LM6000PF; Train 2 was later upgraded to the higher-output LM6000PF+. | ~45-50 MW shaft each (LM6000PF class rating; Train 2 upgraded to the higher-output LM6000PF+; no site-specific figure published) | ~540-600 MW shaft across 12 units (class-rating aggregate) | Aggregate >=50 MW (aeroderivative rule; mechanical drive) -- 12 LM6000PF aeroderivative units aggregate far past the threshold regardless of where the individual unit falls in the ~45-50 MW class range. (Individually the PF/PF+ variant sits at/near 50 MW -- borderline, so the aggregate is the qualifying basis.) | https://www.bakerhughes.com/sites/bakerhughes/files/2020-04/20190130-TEC-WST-LNG19%20LM6000%20Techinical%20Paper.pdf
Papua New Guinea LNG Terminal | T100000130304 | Papua New Guinea | operating; cancelled (unspecified expansion/component only -- the terminal-level facility remains active and operating, so it is not excluded on status) | Multiple aero-derivative gas turbine generators (one held in standby) provide the plant's primary electrical power per PNG LNG's Environmental Impact Statement (Chapter 4, a primary regulatory filing), sized for a base load of 44,267 kW (LNG trains + storage + utilities + offsites + camps) with a design capacity up to 59,760 kW (20% growth + 15% contingency margin). Separately, aero-derivative gas turbines shaft-drive the refrigerant/liquefaction compressors (mechanical drive, no electricity generated). Diesel-engine generators are separate/non-gas, essential/black-start only, and out of scope. | Not itemized per unit | 44.267 MW current base load; design-sized generation capacity up to 59.76 MW | Aggregate >=50 MW (aeroderivative/genset rule) -- JUDGMENT CALL: qualification uses the EIS's design-sized generation capacity (~59.8 MW, built in to accommodate 20% growth + 15% contingency) rather than the 44.267 MW current base load, which alone would fall short of the 50 MW threshold. Flag for review. Separately-documented mechanical-drive turbines shaft-driving the compressors are not MW-quantified and are not needed to reach the qualifying call. | https://www.pnglng.com/media/PNG-LNG-Media/Files/Environment/EIS/eis_chapter04.pdf

## Oceania - Excluded
Terminal | Terminal ID | Country | Reason Excluded | MW Figure (if any) | References
Crib Point FSRU Terminal | T100000130330 | Australia | Cancelled - excluded per instruction. FSRU-mounted dual-fuel engines plus three gas-fired boilers were designed to run the vessel 'electrically isolated from Jetty,' generating its own power as the normal operating arrangement (per AGL/APA's own EES risk assessment), not shore-powered or contingency-only. No turbine/engine model or MW figure is disclosed, so no 'would qualify if active' determination can be made. | None disclosed | https://www.biosphere.org.au/wp-content/uploads/EES-Submission-26-Aug-1.pdf
Darwin LNG Terminal | T100000130331 | Australia | Idled (with a proposed restart/expansion component) -- status stated prominently per the mothballed/idle handling rule, not excluded outright on status. On-site gas turbine power-generation units are documented via a primary operator source (Santos, referenced in connection with a 2019 battery-integration project layered onto the 'existing power generation turbines'), but no individual or aggregate MW figure, unit count, or turbine model is disclosed. | None disclosed | https://www.santos.com/news/darwin-lng/
Ichthys FLNG Terminal | T100000130335 | Australia | No MW figure disclosed. INPEX's own project page states the Bladin Point onshore processing facility includes 'a combined cycle power plant' supplying electricity to the two LNG trains, LPG/condensate plants, and site utilities, but turbine count, model, and MW capacity are not published in this source. | None disclosed | https://www.inpex.com.au/projects/ichthys-lng/
North West Shelf LNG Terminal | T100000130337 | Australia | No MW figure disclosed. Aero-derivative gas turbine generators supply on-site electricity at the Karratha Gas Plant, confirmed as a distinct operating asset class by two independent sources (an offshore-technology.com project profile and a 2026 Boiling Cold cyclone-shutdown report), but turbine model, unit count, and individual/aggregate MW are not itemized in either. | None disclosed | https://www.offshore-technology.com/projects/northwestshelf/, https://www.boilingcold.com.au/cyclone-closes-woodsides-north-west-shelf-australias-largest-gas-plant/
Pluto LNG Terminal | T100000130338 | Australia | No MW figure disclosed. A dedicated gas-fired power generation facility is listed among Pluto LNG's on-site infrastructure, and Woodside's own Q2 2026 report (independently quoted by Energy Aspects) confirms a gas turbine generator synchronised to the on-site 'Pluto power grid' during Train 2 commissioning, but turbine model, count, and MW rating are not itemized in either source. | None disclosed | https://www.nsenergybusiness.com/projects/pluto-lng-expansion-burrup-australia/, https://www.energyaspects.com/resources/insights/pluto-lng-train-2-satellite-commissioning
Prelude FLNG Terminal | T100000130339 | Australia | No MW figure disclosed. Mitsubishi Heavy Industries supplied a dedicated power generation system alongside three compressor trains, and General Electric independently confirms it supplied two steam-turbine-driven compressors (mechanical drive, fed by steam from seven Kawasaki-supplied boilers), but turbine models and MW ratings for both the power-generation system and the mechanical-drive steam turbines are unitemized in either source. | None disclosed | https://www.nsenergybusiness.com/projects/prelude-flng-project/, https://www.ge.com/news/press-releases/ge-technology-selected-worlds-largest-floating-lng-platform
Queensland Curtis LNG Terminal | T100000130340 | Australia | No MW figure disclosed. GE's own press release documents 15 aero-derivative gas turbines driving 28 centrifugal compressors via gearboxes, plus generators, as integral parts of the QCLNG facility -- confirming both mechanical-drive compression and on-site electricity generation -- but individual/aggregate turbine models and MW ratings are not broken out, so the aggregate rule cannot be applied despite the named 'aero-derivative' fleet type. | None disclosed (aero-derivative gas turbines named, but no MW figure available to apply the aggregate rule) | https://www.ge.com/news/press-releases/ge-oil-gas-technology-used-first-ever-large-scale-production-lng-coal-seam-gas-0
Tassie Shoal LNG Terminal | T100000130343 | Australia | Shelved - excluded per instruction. The completed Pre-FEED design (WorleyParsons/Arup, with APCI liquefaction-technology input) specifies LM6000 aero-derivative gas turbine drivers for mechanical-drive refrigeration compression, plus a dedicated on-site 'Power Generation' process module feeding electric-driven compressors; turbine count and MW rating are not disclosed. JUDGMENT CALL: the named LM6000 model carries a general aero-derivative class rating of ~45-50 MW -- borderline at the 50 MW threshold and, unlike Wheatstone's higher-output LM6000PF/PF+ variant, not confidently at or above it -- so a 'would qualify if active' call is NOT made here. Flag for review. | None disclosed (LM6000 class rating ~45-50 MW, borderline against the 50 MW threshold; turbine count unknown) | https://www.melbana.com/site/cpfile/67397a6e-800f-4849-918f-a6856b91ee87/20210602TassieShoalLNGProjectFlyerMelbana.pdf, https://media.abnnewswire.net/media/en/docs/ASX-MEO-382230.pdf
Papua LNG Terminal | T100000130303 | Papua New Guinea | Shelved - excluded per instruction (recorded statuses are proposed and shelved with no operating status, so the project as a whole is treated as shelved at the terminal level). The developer's own site states the project is designed for zero Scope 2 emissions via on-site combined-cycle gas-fired power plant(s) generating all of the facility's electricity (the liquefaction trains use electric-drive compressors, not gas-turbine mechanical drive), but no generator count or MW figure is disclosed. | None disclosed | https://papualng.com.pg/sustainable-development/climate