## Asia - Qualifying (>=50MW)
Terminal | Terminal ID | Country | Status | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | References
Brunei LNG Terminal | T100000130273 | Brunei | operating | On-site fuel-gas-fired energy system at the Lumut plant (nine steam boilers, described by the operator as 'equivalent to a 300 MW power station') driving both mechanical-drive turbine-compressors and generator turbines; co-located 246 MWe Lumut Cogen Power Station, gas-fired, commissioned 1987, operated by Brunei LNG Sdn Bhd itself, supplies electricity and steam to the site. | 246 MWe (Lumut Cogen Power Station, single gas-fired cogen plant, operator-owned) | ~300 MW-equivalent for the boiler-driven energy system per the operator's own description, plus the separate 246 MWe cogen plant | Individual >=50 MW - the co-located 246 MWe Lumut Cogen Power Station, gas-fired and operated by Brunei LNG itself, individually clears the threshold many times over; the boiler-driven mechanical-drive/generator-turbine system (operator-described as 'equivalent to a 300 MW power station') also qualifies. | https://bruneilng.com/the-plant/, https://globalenergyobservatory.org/geoid/45546
Tianjin LNG Terminal (PipeChina) | T100000130410 | China | operating (current chartered FSRU service); retired and construction also recorded among unit-level statuses in the GEM export | FSRU onboard generator fleet: 3x11,400 kW + 1x5,700 kW dual-fuel gensets, plus 2x13,200 kW turbo/electric generators fed by dual-fuel main boilers (mainly natural gas, secondary low-sulfur diesel); a separate 500 kW emergency diesel genset is non-gas and excluded from the total. | 13.2 MW max individual unit (turbo/electric generator); largest genset is 11.4 MW - no single unit reaches 50 MW | 66.3 MW aggregate across gas-fired units (3x11.4+1x5.7 MW gensets = 39.9 MW, plus 2x13.2 MW turbo-generators = 26.4 MW; the 500 kW emergency diesel is excluded) | Aggregate >=50 MW (genset rule) - dual-fuel gensets and boiler-fed turbo/electric generators aboard the FSRU total 66.3 MW gas-fired capacity, well above the 50 MW aggregate threshold; individual units are all well under 50 MW. | https://www.mee.gov.cn/ywgz/hjyxpj/jsxmhjyxpj/xmslqk/201605/W020160522142436760339.pdf
Karaikal FSRU | T100000130803 | India | proposed | 3x22 MW gas turbine generators (66 MW aggregate) with SCR NOx control and waste heat recovery units, described as coming 'as part of the FSU' - the floating storage unit's own onboard power plant, for the proposed Karaikal LNG terminal. | 22 MW each - below the 50 MW individual threshold | 66 MW aggregate (3x22 MW gas turbine generators) | Aggregate >=50 MW (aeroderivative/genset-style rule applied by analogy to 3 parallel mid-size gas turbine generator units) - JUDGMENT CALL: the source does not state whether these are heavy-duty single-train turbines (individual-unit rule) or aeroderivative/genset-style redundant units (aggregate rule); flagged for review. | https://environmentclearance.nic.in/writereaddata/Form-1A/EC/11082018119327KaraikalPortECLetter.PDF
West Papua FLNG Terminal | T100000131148 | Indonesia | construction | Wison New Energies standard FLNG design: 2xLM6000PF+ aeroderivative gas turbines (with waste-heat recovery) mechanically drive the refrigerant compressors; 1xLM2500 aeroderivative turbine mechanically drives NGL-recovery booster compression; Solar Titan 130 aeroderivative gas turbine generators (with WHR) provide site power generation. | ~45-50 MW each for the 2xLM6000PF+ mechanical-drive units (LM6000 aeroderivative class rating per convention; no site-specific figure published); LM2500 booster-compression unit ~25-34 MW class; Solar Titan 130 power-generation units' rating not specified in source. | ~90-100 MW aggregate across the 2xLM6000PF+ mechanical-drive turbines (aeroderivative rule) | Aggregate >=50 MW (aeroderivative rule, mechanical drive) - 2xLM6000PF+ aeroderivative gas turbines mechanically driving refrigerant compressors aggregate to an estimated 90-100 MW at the standard LM6000 class rating; class inferred from the named turbine model, no site-specific figure published (JUDGMENT CALL - class-rating inference). | https://www.gastechevent.com/media/zoppuuti/damian-nguyen_wison-new-energies_2094.pdf, https://www.genting.com/wp-content/uploads/2024/10/GENT-Press-Release-on-Procurement-Contract-and-CIC-Contract-for-Genting-FLNG-project.pdf, https://klse.i3investor.com/web/blog/detail/ceomorningbrief/2024-10-29-story-h472823971-Genting_Commissions_Contractors_to_Build_Midstream_Infra_to_Link_Kasuri_
Dua FLNG Terminal | T100000130289 | Malaysia | operating | PFLNG DUA (moored offshore FLNG vessel): 4xGE PGT25+G4 aeroderivative gas turbine generator systems supply the facility's electric power; 2xLM6000-PF+ 2BCL907 aeroderivative gas turbines mechanically drive the nitrogen-liquefaction-train compressors. Both installed under GE Oil & Gas's November 2014 turbomachinery contract. | ~45-50 MW each for the 2xLM6000-PF+ mechanical-drive units (LM6000 aeroderivative class rating per convention; no site-specific figure published); PGT25+G4 power-generation units' individual rating not specified in source. | ~90-100 MW aggregate across the 2xLM6000-PF+ mechanical-drive turbines (aeroderivative rule); 4xPGT25+G4 power-generation turbines aggregate separately, MW not stated in source. | Aggregate >=50 MW (aeroderivative rule, mechanical drive) - 2xLM6000-PF+ aeroderivative turbines drive the nitrogen-train compressors at an estimated 90-100 MW aggregate (LM6000 class rating, JUDGMENT CALL - class-rating inference); separately confirms 4xPGT25+G4 aeroderivative generators for site power generation (MW not stated). | https://www.ge.com/news/press-releases/ge-oil-gas-supplying-malaysias-petronas-turbomachinery-second-floating-lng-facility, https://www.offshore-technology.com/projects/pflng-2-rotan-flng-project-sabah/
MLNG T9 LNG Terminal | T100000130293 | Malaysia | operating | 2xGE Frame 7EA heavy-duty gas turbines (mechanical drive), each paired with a 13 MW induction motor (VSI/VSD, 3,600 rpm) as a helper/assist unit, drive Train 9's LP/MP mixed-refrigerant and propane/HP mixed-refrigerant compression trains. The wider Bintulu Petronas LNG Complex also self-generates a portion of its electricity via on-site gas turbines. | ~85-90 MW shaft each (GE Frame 7EA class rating; no site-specific figure published) for the mechanical-drive turbines; the paired 13 MW motor is a helper/assist unit driving alongside, not a separate qualifying generator. | n/a (mechanical drive, heavy-duty individual-unit rule, not summed - combined class rating would be roughly 170-180 MW across both units) | Individual >=50 MW (mechanical drive; Frame 7EA class-rating inference, JUDGMENT CALL - class rating inferred from the named turbine model, no site-specific figure published). | https://www.ge.com/news/press-releases/petronas-selects-ge-technology-petronas-lng-train-9-project, https://www.offshore-energy.biz/malaysia-petronas-picks-ge-technology-for-lng-train-9-project/, https://www.petronas.com/flow/sustainability/sparking-sustainable-future-electrifying-petronas-lng-complex
Satu FLNG Terminal | T100000130288 | Malaysia | operating | PFLNG SATU (moored at the Kanowit field, off-grid by construction): 4x GE PGT25+G4 gas turbine generator sets supply on-site electricity, plus 2x PGT25+G4 gas turbines in mechanical-drive service on the liquefaction compression trains (alongside 2 electric-motor-driven compressor modules). | ~30-34 MW each (PGT25+G4 = industrial LM2500+G4; class rating, no site-specific figure published) | ~120-136 MW generator fleet (4 units); ~200 MW including the 2 mechanical-drive units (class-rating aggregate) | Aggregate >=50 MW (aeroderivative rule; PGT25+G4 is the industrial LM2500+G4 aeroderivative -- same class-inference basis as the Cameroon FLNG and Corpus Christi qualifiers). Individual units (~30-34 MW) are below threshold; the aggregate is the qualifying basis. | https://www.ge.com/news/press-releases/petronas-selects-ges-compressor-technology-asias-first-floating-lng-project-0
Tiga FLNG Terminal | T100000131063 | Malaysia | construction | Purpose-built onshore gas-fired power plant at Sipitang (Sabah), adjacent to PFLNG Tiga's nearshore mooring: 7xMAN Energy Solutions 20V35/44G gas engines, described by both the equipment vendor and independent trade press as becoming the sole electricity supply to the terminal. | 10 MW each (70 MW / 7 engines) - below the 50 MW individual threshold | 70 MW aggregate (7xMAN 20V35/44G gas engines) | Aggregate >=50 MW (genset rule) - 7 gas engines totaling 70 MW, explicitly the sole electricity supply to the terminal; well above the 50 MW aggregate threshold. | https://www.man-es.com/company/press-releases/press-details/2024/09/04/man-energy-solutions-to-supply-gas-engines-for-three-power-plants-in-southeast-asia, https://www.rivieramm.com/news-content-hub/news-content-hub/malaysia-gears-up-for-third-flng-project-82285, https://www.thestar.com.my/business/business-news/2024/04/01/petronas-begins-the-construction-of-its-third-floating-lng-facility

## Asia - Excluded
Terminal | Terminal ID | Country | Reason Excluded | MW Figure (if any) | References
Moheshkhali Floating LNG Terminal | T100000130270 | Bangladesh | No MW figure disclosed. Two boil-off-gas-fired boilers aboard FSRU Excellence supply the vessel's own electrical power for regasification pumps and other loads (confirmed by a July 2026 fire that damaged the boiler power/control cabling and forced a nationwide gas-supply cut); general FSRU-conversion literature suggests a 15-25 MW class range but no site-specific rating was found. | None disclosed (general FSRU literature suggests 15-25 MW class, not site-specific) | https://www.tbsnews.net/bangladesh/gas-crisis-deepens-lng-terminal-outage-disrupts-supply-cripples-household-cooking-1498596, https://thereport.live/bangladesh/gas-crisis-deepens-as-fsru-fire-disrupts-supply-relief-not-expected-soon/41055
Summit FSRU | T100000130272 | Bangladesh | Below the 50 MW threshold. 2x10 MW-class gas turbine generators (1 operating + 1 standby) supply the FSRU's captive power per the project EIA, which labels it a 'captive power generation facility'; only one unit runs at a time (10 MW), and even the full 2-unit nameplate (20 MW) does not clear the threshold. | 20 MW aggregate nameplate (2x10 MW-class gas turbine generators, 1 operating + 1 standby) | https://www.nexi.go.jp/environment/info/pdf/18-022_EIA_01.pdf
Hong Kong FSRU | T100000130388 | Hong Kong | Aggregate reported only as a floor value, not confirmed to clear 50 MW. 4xMAN 9L51/60 dual-fuel generators aboard the Bauhinia Spirit FSRU are each rated '>9 MW,' stated as '>36 MW aggregate' - a lower bound, not a precise figure, so it cannot be confirmed to reach the 50 MW threshold. | >36 MW aggregate (4xMAN 9L51/60 dual-fuel generators, each >9 MW; precise total not disclosed) - JUDGMENT CALL, treated as below threshold absent a confirmed figure | https://marine-offshore.bureauveritas.com/magazine/explore-mols-fsru-bauhinia-spirit-bureau-veritas
Chhara LNG Terminal | T100000130800 | India | Below the 50 MW threshold. An 18 MW gas-turbine-based captive power plant (CPP) is the terminal's primary power source per its Risk Assessment/EIA, with the Gujarat State grid as standby and an emergency diesel generator as further backup. | 18 MW (gas-turbine-based captive power plant) | https://environmentclearance.nic.in/writereaddata/online/RiskAssessment/030120170Q1QDMZ8RiskAssessment.pdf
Dahej LNG Terminal | T100000130427 | India | Below the 50 MW threshold based on the only figure available. Three GTG packages form Petronet's on-site captive power plant per an EPC technical specification (no MW stated there); media reporting (not independently verified this pass) puts existing capacity at roughly 25 MW aggregate - well under the threshold either way. | ~25 MW aggregate (media estimate, not independently verified this pass; the primary EPC technical spec does not itself state an MW figure) | https://pdfcoffee.com/a324-00-tg-sp-0030-pdf-free.html, https://www.adb.org/sites/default/files/project-documents/39921-ind-siee.pdf
Dhamra LNG Terminal | T100000130431 | India | Below the 50 MW threshold. Three 9.6 MW gensets (29 MW total) based on 20-cylinder Rolls-Royce Bergen B35:40 gas engines, delivered as a full EPC gas power plant to meet the terminal's baseload power requirement. | 29 MW aggregate (3x9.6 MW gensets) | https://www.rolls-royce.com/media/press-releases/2020/06-10-2020-rr-to-deliver-29-mw-gas-power-plant-for-dhamra-lng-regasification-terminal-in-india.aspx, https://www.dtnext.in/news/business/rollsroyce-to-deliver-29-mw-gas-power-plant-for-dhamra-lng-terminal, https://www.cnbctv18.com/energy/rolls-royce-to-deliver-29-mw-gas-power-plant-to-dhamra-lng-terminal-7118821.htm
Ennore LNG Terminal | T100000130662 | India | Below the 50 MW threshold. On-site captive combined-heat-and-power plant using gas turbine generators, rated 27 MW by the EPC contractor (Black & Veatch) or 26 MW per IndianOil LNG's own post-expansion power-balance filing (14 MW existing + 12 MW for the 5->10 MMTPA expansion). | 26-27 MW (captive CHP gas turbine plant; EPC contractor figure vs. operator filing) | http://indianoillng.com/wp-content/uploads/2026/07/IOLPL-Expansion-EC-CRZ-Clearance.pdf, https://www.bv.com/projects/ennore-lng-terminal-black-and-veatch-completes-design-to-commissioning-of
Gopalpur LNG Terminal | T100000131145 | India | No MW figure disclosed. GTGs for captive power are named as a Phase-II land-based-terminal design element (item 25 of 26) in Petronet's MoEFCC Terms of Reference for the proposed terminal; model, count, and MW rating are not stated. Current Phase-I power needs are grid-fed from the Chhatrapur substation, separate from this Phase-II design element. | None disclosed | https://parivesh.nic.in/certificates/PETRONET_LNG_LIMITED_(PLL)/5/4312635/specific_tor_IA_OR_INFRA1_424189_2023_4312636_-signed.pdf
Jafrabad FSRU | T100000130457 | India | Below the 50 MW threshold. 4xWartsila-Hyundai W9L50DF dual-fuel DFDE generator sets, 8,775 kW each (35.1 MW total), aboard the assigned FSRU vessel (Vasant 1) supply the vessel's hotel load, propulsion, and the regasification process. | 35.1 MW aggregate (4x8,775 kW dual-fuel DFDE gensets) | https://eplan.irclass.org:8090/IRS_Ship_Info.aspx?Imo_no=9837066
Jaigarh LNG Terminal | T100000130443 | India | Below the 50 MW threshold. 4xWartsila-Hyundai dual-fuel DFDE generator sets (1x6L50DF + 3x8L50DF) totaling 28,500 kW aboard the Phase-I FSRU (Hoegh Giant), supplying propulsion, hotel load and the regasification train while moored. | 28.5 MW aggregate (4 dual-fuel DFDE gensets) | https://www.ship-db.de/nawbn.php?wbn_nr=HYHU2552010E
Kochi LNG Terminal | T100000130447 | India | Below the 50 MW threshold. A 13 MW on-site captive gas turbine generator (GTG) plant supplies part of the terminal's power, topped up by Kerala State Electricity Board grid import; a separate 1.6 MVA diesel emergency DG set is backup-only and non-gas. | 13 MW (captive gas turbine generator plant; partial supply alongside grid) | https://environmentclearance.nic.in/auth/FORM_A_PDF.aspx?cat_id=IA/KL/IND2/229000/2021, https://petronetlng.in/documents/d/pertonetlng/nit_39?download=true
Bontang LNG Terminal | T100000130278 | Indonesia | No MW figure disclosed for the primary on-site mechanical-drive system (gas-fired boilers driving a steam turbine that runs the refrigerant compressor); a separately documented 13.4 MW gas turbine at the plant (per its own 1998 equipment data book) falls below the 50 MW threshold on its own. Terminal-level status is mixed (retired/idled/cancelled recorded among unit-level statuses in GEM data, but the mechanical-drive system remains operating/active, so this is not a status-gate exclusion). | 13.4 MW documented gas turbine (below threshold on its own); no MW figure disclosed for the primary boiler/steam-turbine mechanical-drive system | https://www.dunia-energi.com/collaborating-with-pln-badak-lng-encourages-innovation-to-increases-efficiency/, https://api.crossref.org/works/10.1063/5.0073900
Lampung FSRU | T100000130283 | Indonesia | No vessel-specific MW figure disclosed. PGN FSRU Lampung is managed by Hoegh LNG Fleet Management and described only via a fleet-wide company statement that Hoegh's FSRUs use dual-fuel diesel-electric (DFDE) generator sets; a sister vessel's rating (Hoegh Esperanza, 4x7,800 kW = 31.2 MW) is explicitly NOT attributed to this hull in the source. | None disclosed for this vessel (sister-vessel reference of 31.2 MW aggregate explicitly not attributed to Lampung) | https://www.rivieramm.com/news-content-hub/hoegh-lng-takes-delivery-of-its-ninth-fsru-22463, https://directory.marinelink.com/ships/ship/pgn-fsru-lampung-5559
Tangguh LNG Terminal | T100000130286 | Indonesia | No MW figure disclosed for the on-site captive system. Heavy-duty gas turbines mechanically drive the LNG-train refrigeration compressors, and their waste heat is recovered via HRSG to generate electricity used internally, with a small surplus (4 MW) historically sold to PLN; exact turbine model/count and total generating MW are not disclosed in sources found. | None disclosed (only ancillary figure found is 4 MW historically sold to PLN, not the total on-site captive capacity) | https://www.adb.org/sites/default/files/project-documents//49222-001-esia-03.pdf, https://turbomachinerymag.com/view/baker-hughes-signs-parts-repair-engineering-contract-for-tangguh-lng
Tanjung Benoa FSRU | T100000130276 | Indonesia | No MW figure disclosed. The FSRU Karunia Dewata carries a dual-fuel (DFDE-type) auxiliary generator set with a SOGAV gas-admission fuel system, confirmed gas-fired by a 2025 maritime-academy thesis documenting a 2022 fault incident, but no nameplate rating is published. | None disclosed | http://eprints.pipmakassar.ac.id/1239/
Hatsukaichi LNG Terminal | T100000130473 | Japan | Below the 50 MW threshold. 2xMHIET KU30GA natural gas engines, 5,500 kW each (11 MW total), gas-engine cogeneration installed 2004 (retrofitted 2018) to power the terminal's own refrigeration/vaporization load, with surplus power wheeled to the grid. | 11 MW aggregate (2x5,500 kW gas-engine cogeneration units) | https://www.hiroshima-gas.co.jp/com/w_new/new03_11/hatsu_c.htm, https://www.mhi.com/jp/group/mhiet/news/20181128.html
Naoetsu LNG Terminal | T100000130505 | Japan | No MW figure disclosed. On-site gas turbine generator is one of two non-normal/emergency power sources (the other diesel) backing up the dual utility grid feed at INPEX's Naoetsu terminal (standby_backup category); count, model and MW are not published. | None disclosed (standby/emergency-duty gas turbine generator; count and model undisclosed) | https://www.tmeic.co.jp/column/p2_vol03/
Yokkaichi Works LNG Terminal | T100000130533 | Japan | Below the 50 MW threshold. 3x5,500 kW gas-engine cogeneration units (16.5 MW total) at Toho Gas's own Yokkaichi Works, commissioned Oct 2017 explicitly for internal power-demand balancing, with waste heat feeding on-site city-gas manufacturing. | 16.5 MW aggregate (3x5,500 kW gas-engine cogeneration units) | https://www.tohogas.co.jp/corporate-n/press/1205024_1342.html, https://www.nikkan.co.jp/articles/view/444977
Yoshinoura LNG Terminal | T100000130837 | Japan | Below the 50 MW threshold. The 35,000 kW (35 MW) Yoshinoura Multi-Gas-Turbine plant (LNG-primary multi-fuel) provides island blackstart, LNG-tank security backup, peak-demand response, and BOG-processing duty for the terminal, but total plant capacity is 35 MW. | 35 MW (Yoshinoura Multi-Gas-Turbine plant total) | https://ja.wikipedia.org/wiki/%E5%90%89%E3%81%AE%E6%B5%A6%E7%81%AB%E5%8A%9B%E7%99%BA%E9%9B%BB%E6%89%80, https://release.itmedia.co.jp/release/sj/2015/03/20/3d55355e70e6ae850423a801da9c05e6.html
MLNG Dua LNG Terminal | T100000130292 | Malaysia | No MW figure disclosed at the individual-terminal/train level. Complex-wide, Petronas states the Bintulu complex relied 'solely on gas-powered turbines' before a 2024 grid tie-in (Project GLORY) substituted 40%/90 MW of total demand with Sarawak hydro, leaving the majority still gas-turbine-generated jointly across MLNG, MLNG Dua and MLNG Tiga - not apportioned to this terminal specifically. JUDGMENT CALL: complex-level context is suggestive but not documented per train. | None disclosed at the individual-terminal level (complex-wide majority of >~135 MW implied gas-turbine demand shared across 3 terminals, per the Project GLORY 90 MW/40% substitution figure) | https://www.petronas.com/flow/sustainability/sparking-sustainable-future-electrifying-petronas-lng-complex, https://www.ge.com/news/press-releases/ge-wins-1276-million-service-contract-malaysia-lng-complex, https://lngprime.com/lng-terminals/sarawak-energy-to-power-petronas-bintulu-lng-complex/13808/
MLNG Satu LNG Terminal | T100000130294 | Malaysia | No MW figure disclosed at the individual-terminal/train level. Complex-wide, Petronas states the Bintulu complex relied 'solely on gas-powered turbines' before a 2024 grid tie-in (Project GLORY) substituted 40%/90 MW of total demand with Sarawak hydro, leaving the majority still gas-turbine-generated jointly across MLNG, MLNG Dua and MLNG Tiga - not apportioned to this terminal specifically. JUDGMENT CALL: complex-level context is suggestive but not documented per train. | None disclosed at the individual-terminal level (complex-wide majority of >~135 MW implied gas-turbine demand shared across 3 terminals, per the Project GLORY 90 MW/40% substitution figure) | https://www.petronas.com/flow/sustainability/sparking-sustainable-future-electrifying-petronas-lng-complex, https://www.ge.com/news/press-releases/ge-wins-1276-million-service-contract-malaysia-lng-complex, https://lngprime.com/lng-terminals/sarawak-energy-to-power-petronas-bintulu-lng-complex/13808/
MLNG Tiga LNG Terminal | T100000130295 | Malaysia | No MW figure disclosed at the individual-terminal/train level. A GE long-term service agreement names MLNG, MLNG Dua and MLNG Tiga jointly as covering 'the power generation units and liquefaction trains' for the complex; Petronas' own electrification account confirms the wider complex traditionally self-generated its power via on-site gas turbines (now ~40%/90 MW substituted by Sarawak grid hydro), but no MW figure is apportioned to this terminal specifically. JUDGMENT CALL: complex-level context is suggestive but not documented per train. | None disclosed at the individual-terminal level (complex-wide majority of >~135 MW implied gas-turbine demand shared across 3 terminals, per the Project GLORY 90 MW/40% substitution figure) | https://www.ge.com/news/press-releases/ge-wins-1276-million-service-contract-malaysia-lng-complex, https://www.petronas.com/flow/sustainability/sparking-sustainable-future-electrifying-petronas-lng-complex