## EU - Qualifying (>=20MW)
Terminal | Terminal ID | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | Turbine/Genset Class | References
Toscana FSRU | T100000130474 | Onboard BOG-fired steam power plant aboard FSRU Toscana: boilers normally burning boil-off gas feed 2x10 MW plus 2x3.35 MW steam turbogenerators; the terminal is energy self-sufficient ~22 km offshore with no shore-power connection (diesel gensets emergency-only). | 10 MW (largest units); 3.35 MW (smaller pair) | 26.7 MW total gas-fired | Aggregate >=20 MW (onboard steam-turbogenerator plant, BOG-fired; aggregate treatment is a judgment call - steam TGs are neither aeroderivative nor gensets, cf. the Constanta exclusion, but as a self-contained offshore island plant the fleet aggregates like a genset set) | Steam turbogenerator (BOG-fired boilers) | https://va.mite.gov.it/File/Documento/135472 https://va.mite.gov.it/File/Documento/42972

## EU - Excluded
Terminal | Terminal ID | Reason Excluded | MW Figure (if any) | References
Trieste Monfalcone LNG Terminal | T100000130482 | Cancelled - excluded per instruction. 2006 EIA design: offshore GBS terminal energy self-sufficient via 3 gas-turbine-driven electric generators (~16 MW each, 2 duty + 1 spare), diesel sets startup/emergency only - would qualify on aggregate if active. | ~48 MW installed / ~32 MW duty (3x~16 MW, design) | https://va.mite.gov.it/File/Documento/3068

## Russia - Qualifying (>=50MW)
Terminal | Terminal ID | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | Turbine/Genset Class | References

## Russia - Excluded
Terminal | Terminal ID | Reason Excluded | MW Figure (if any) | References
Shtokman LNG Terminal | T100000130514 | Cancelled/frozen - excluded per instruction. Published design for the Teriberka LNG plant included a dedicated own-needs ('sobstvennykh nuzhd') gas-turbine power station of 600 MW using 110+ MW-class units (2009 construction tender); independent academic analysis corroborates the same solution class (4x GTE-110, 442 MW) - would qualify both ways if active. | 600 MW (design; 110+ MW-class units) | https://cyberleninka.ru/article/n/potentsial-energosberezheniya-gazoturbinnoy-elektrostantsii-pri-realizatsii-pervoy-stadii-shtokmanovskogo-proekta https://ru.thebarentsobserver.com/tender-na-stroitelstvo-elektrostancii-v-teriberke/300953

## Americas - Qualifying (>=50MW)
Terminal | Terminal ID | Country | Status | Hardware Type | Individual Unit MW | Aggregate/Total MW | Qualifying Basis | References
Cameron LNG Terminal | T100000130214 | USA | operating (T1-3); proposed (T4) | Frame 7-class gas turbines shaft-driving the propane and mixed-refrigerant compressors on Trains 1-3 (mechanical drive, no electricity generated). Proposed Train 4 switches to 3x electric E-Drive motors (up to 75 MW each), so T4 itself is not captive. | ~85-90 MW shaft each (Frame 7 class; no site-specific figure published) | n/a (mechanical drive, not summed) | Individual >=50 MW (mechanical drive) | https://cameronlng.com/lng-facility/lng-and-liquefaction/ https://gascompressionmagazine.com/2022/03/21/cameron-lng-expansion-requests-train-4-enhancement/
Corpus Christi LNG Terminal | T100000130216 | USA | operating (T1-3); construction/proposed (Stage 3) | GE LM2500+G4 / Baker Hughes PGT25+G4 aeroderivative gas turbines mechanically driving the propane/ethylene/methane refrigerant compressors on Trains 1-3 (Optimized Cascade). Stage 3 reportedly shifts to motor-driven compressors. | ~34 MW shaft each (LM2500+G4 class) | 18 drivers across T1-3 (~600 MW shaft class) | Aggregate >=50 MW (aeroderivative rule; mechanical drive) | https://archive.epa.gov/region6/6pd/air/pd-r/ghg/web/pdf/corpuschristi-liq-turbine-simple-cycle060613.pdf https://www.bakerhughes.com/company/news/bhge-wins-turbomachinery-contract-cheniere-energy-incs-lng-facility-corpus-christi
Golden Pass LNG Terminal | T100000130227 | USA | operating; construction | Six GE/Baker Hughes MS7001EA (Frame 7EA) heavy-duty gas turbines shaft-driving 12 refrigerant compressors across 3 trains; BOG compression on separate ~6.8 MW electric motors. | ~85-90 MW shaft each (Frame 7EA class) | n/a (mechanical drive, not summed) | Individual >=50 MW (mechanical drive) | https://www.bakerhughes.com/company/news/baker-hughes-ge-company-supply-turbomachinery-equipment-golden-pass-lng-export https://www.hydrocarbonengineering.com/tanks-terminals/11022019/bhge-to-supply-turbomachinery-equipment-for-golden-pass-lng-export-facility/
Rio Grande LNG Terminal | T100000130239 | USA | construction (T1-5); proposed (expansion) | Frame 7 heavy-duty gas turbines directly coupled to the main refrigerant compressors across Trains 1-5 (Optimized Cascade); no electric-drive/grid language in any source. | ~85-90 MW shaft each (Frame 7 class; no project-specific figure published) | n/a (mechanical drive, not summed) | Individual >=50 MW (mechanical drive) | https://www.globenewswire.com/news-release/2025/09/11/3148922/0/en/Baker-Hughes-Secures-Order-for-Rio-Grande-LNG-Expansion.html https://www.lngindustry.com/liquefaction/15092025/baker-hughes-to-supply-main-liquefaction-equipment-for-rio-grande-lng-expansion/ https://www.worldoil.com/news/2025/11/6/baker-hughes-wins-order-for-nextdecade-s-rio-grande-lng-train-5-expansion/
Port Arthur LNG Terminal | T100000130237 | USA | construction | FERC-certified on-site gas-turbine generator fleet (240 MW) PLUS four GE Frame 7 gas turbines mechanically driving the eight main refrigerant compressors (Phase 1). | Generators not broken out; Frame 7 mechanical drives ~85 MW shaft class each | 240 MW (FERC-certified generation) | Qualifies both ways (aggregate generation AND individual mechanical drive) | https://www.ferc.gov/sites/default/files/2020-04/C-3.pdf https://www.lngindustry.com/liquefaction/28032023/baker-hughes-to-supply-liquefaction-trains-for-sempra-infrastructures-port-arthur-lng-phase-1-project/
Freeport LNG Terminal | T100000130224 | USA | operating | Dedicated gas-turbine generator at the on-site Pretreatment Facility (Quintana, TX), normally fueled by boil-off gas piped from the liquefaction plant, with waste-heat recovery to the three pretreatment trains. The main T1-T4 liquefaction trains are electric-motor-driven (3x 75 MW GE motors per train) and grid-fed via ERCOT - NOT captive. | ~50 MW (nameplate not disclosed; the unit exported ~50 MW to ERCOT during the Jun-Oct 2022 outage while normally also carrying house load, so nameplate is at least ~50 MW) | ~50 MW (single unit) | Individual ~>=50 MW (observed grid export; nameplate undisclosed - borderline, flagged for review) | https://freeportlng.com/index.php?p=our-business/elng/ https://gasprocessingnews.com/news/2022/07/freeport-lng-plant-pulls-in-natgas-to-produce-power-for-texas/ https://www.epa.gov/sites/default/files/2018-03/documents/tx0134056_statement_of_basis.pdf
Magnolia LNG Terminal | T100000130234 | USA | proposed | Two 33 MW gas turbines per liquefaction train directly driving the mixed-refrigerant compressors (OSMR; mechanical drive). On-site electricity generation explicitly ruled out in design; remaining 6.5 MW/train electrical load grid-fed via a new 230-kV Entergy line. | 33 MW shaft each | 66 MW shaft per train; 264 MW across 4 trains | Aggregate >=50 MW (mechanical drive) | https://www.energy.gov/sites/default/files/2015/11/f27/EIS-0498_Magnolia_LNG_FEIS_%28Nov_2015%29.pdf
ST LNG FLNG Terminal | T100001061236 | USA | proposed | Off-grid by design (MARAD DWP application): 16x Baker Hughes NovaLT16 gas turbine generators project-wide (4/phase incl. one standby) plus 8x Siemens SGT-750 gas turbines as MR compressor mechanical drives. | 16.9 MW each (NovaLT16) | 270.4 MW installed generation (~202.8 MW at normal N+1 load), plus 8x SGT-750 mechanical drive | Aggregate >=50 MW (genset-style generator fleet; also mechanical drive) | https://downloads.regulations.gov/MARAD-2025-0096-0001/attachment_1.pdf https://downloads.regulations.gov/MARAD-2025-0096-0028/attachment_1.pdf

## Americas - Excluded
Terminal | Terminal ID | Country | Reason Excluded | MW Figure (if any) | References
Gulf LNG Terminal | T100000130228 | USA | Below threshold - the operating import terminal is grid-fed (Mississippi Power, 23 kV) with only two 12 MW essential-backup gas turbine generators on site. The FERC-authorized liquefaction expansion (never built) would add four mechanical-drive gas turbines (two per train), but no MW rating is disclosed in any verified source. | 24 MW (2x12 MW backup GTGs at the import terminal) | https://www.energy.gov/sites/prod/files/2019/04/f62/final-eis-0504-gulf-lng-2019-04-chp-2.pdf https://www.ferc.gov/sites/default/files/CalendarFiles/20190716201154-CP15-521-000.pdf https://www.nsenergybusiness.com/projects/kinder-morgans-gulf-lng-export-project/
Lake Charles LNG Terminal | T100000130232 | USA | Shelved project - excluded per instruction. As-designed, the export trains use on-site gas turbines to mechanically drive the MR compressors (no on-site generation; facility load grid-fed via a new 230-kV Entergy line, diesel-only standby gensets). No turbine MW disclosed. | None disclosed (mechanical drive) | https://www.energy.gov/sites/prod/files/2015/08/f26/EIS-0491-FEIS-2015.pdf
G2 LNG Terminal | T100000130226 | USA | Cancelled - excluded per instruction. Design integrated a NET Power Allam-Fetvedt gas-fired power island (300 MW per module, >1,000 MW across the full build) - would qualify on aggregate if the project were active. | 300 MW per module (design; >1,000 MW full build) | https://lngprime.com/americas/g2-net-power-ink-new-deal-for-louisiana-lng-export-project/19753/ https://www.lngindustry.com/special-reports/11052021/g2-and-net-power-collaborate-on-net-zero-lng-project/ https://www.offshore-energy.biz/g2-advances-its-net-zero-lng-export-project/
Jordan Cove LNG Terminal | T100000130230 | USA | Cancelled - excluded per instruction. FERC FEIS design: direct-drive gas turbines on the refrigeration compressors with waste-heat recovery (HRSG) feeding a steam turbine-generator for facility power (superseded the earlier 420 MW South Dunes combined-cycle concept). No MW rating disclosed for the final design. | None disclosed (earlier concept: 420 MW CCGT) | https://www.ferc.gov/sites/default/files/2020-05/11-15-19-FEIS_Part_1.pdf
Delta LNG Terminal | T100000130985 | USA | Cancelled/withdrawn (June 2025, in favor of expanding adjacent Plaquemines LNG) - excluded per instruction. Published design named a dedicated on-site 'gas-powered power plant' as a distinct component, but no turbine model, unit count, or MW rating was found in any verifiable source. | None disclosed | https://www.offshore-technology.com/news/venture-global-withdraws-delta-lng-project/
Grand Isle Deepwater Port Terminal | T100000131129 | USA | Cancelled - excluded per instruction. 2023 MARAD deepwater-port license application: no grid connection; simple-cycle gas turbine generators would supply all facility power. No MW rating disclosed. | None disclosed | https://downloads.regulations.gov/MARAD-2023-0119-0003/attachment_5.pdf
Port Pelican LNG Terminal | T100000130647 | USA | Cancelled - excluded per instruction. Deepwater Port License Application specified three LM2000 gas-turbine generators (BOG-fueled, one as backup) as main power at 13.8 kV; diesel gensets emergency-only. | ~18 MW class x3 (~54 MW aggregate, class rating - not project-stated) | https://downloads.regulations.gov/USCG-2002-14134-0002/attachment_1.pdf
Main Pass Energy Hub FLNG Terminal | T100000130636 | USA | Cancelled - excluded per instruction. Baker Hughes LM9000 aeroderivative gas turbines selected (2018) for the 2x Liqui-Max FLNG vessels; unit count and electric rating for this project never published. | LM9000 class ~65-73 MW each (class rating only) | https://www.bakerhughes.com/gas-turbines/aeroderivative-technology/lm9000-aeroderivative-gas-turbine https://www.lngindustry.com/liquid-natural-gas/26062018/gls-advances-mpeh-lng-export-project/ https://www.offshore-energy.biz/gls-selects-bhge-gas-turbines-for-its-main-pass-lng-project/
Neptune LNG Terminal | T100000130633 | USA | Below threshold (and mothballed). EPA deepwater-port application documents the shuttle/regas vessels' onboard dual-fuel power-generation engines, 2x11,400 kW, operable in gas mode. | 22.8 MW (2x11.4 MW) | https://www.epa.gov/caa-permitting/permit-documents-neptune-deepwater-port-federal-waters-massachusetts-bay-lng https://www.epa.gov/sites/default/files/2015-08/documents/ndp-application.pdf
Northeast Gateway FSRU | T100000130632 | USA | No MW figure disclosed (and idled). EBRV vessels carry onboard steam turbine generators fed by MHI dual-fuel boilers burning boil-off/natural gas during regas operations. | None | https://www.epa.gov/caa-permitting/permit-documents-northeast-gateway-energy-bridge https://www.epa.gov/sites/default/files/2015-08/documents/ngeb-application.pdf
Ocean Cay LNG Terminal | T100000130544 | Bahamas | Cancelled - excluded per instruction (also below threshold). Design: three 15 MW gas-fired turbine generators for the facilities' own power; project abandoned by 2009 at the design/EIA stage. | 45 MW (3x15 MW, design) | https://www.offshore-technology.com/projects/oceancaylngterminala/
Aurora LNG Terminal | T100000130346 | Canada | Cancelled - excluded per instruction. 2014 federal Project Description: gas-turbine-driven refrigerant compressors plus likely on-site gas-fired self-generation (est. 120-300 MW Phase 1 / 200-550 MW full build; type/capacity was to be set in FEED). | est. 120-550 MW (design estimate only) | https://iaac-aeic.gc.ca/050/documents/p80075/99505E.pdf
Bear Head LNG Terminal | T100000130347 | Canada | Cancelled - excluded per instruction. OSMR design (sister project to Magnolia LNG): aero-derivative gas turbines driving the refrigeration compressors plus a CHP plant for facility power. No MW disclosed. | None disclosed | https://www.offshore-technology.com/projects/bear-head-lng-project-richmond-county-nova-scotia/
Goldboro LNG Terminal | T100000130354 | Canada | Cancelled - excluded per instruction. NS Environmental Assessment registration listed a dedicated 180 MW open-cycle gas-turbine power plant (Frame 6, N+1) feeding electric-motor-driven compressors, plus separate Frame 7 mechanical-drive turbines (~160 MW class) on the two trains - would qualify if active. | 180 MW plant (design) + Frame 7 mechanical drive | https://novascotia.ca/nse/ea/goldboro-lng/00-Executive-Summary.pdf https://novascotia.ca/nse/ea/goldboro-lng/03-Project-Description.pdf https://novascotia.ca/nse/ea/goldboro-lng/goldboro-panel-report-2014-03-07.pdf
Kwispaa LNG Terminal | T100000130366 | Canada | Cancelled - excluded per instruction. BC EAO Initial Project Description described an on-site gas-fired power generation facility (up to ~500 MW per 12-mtpa phase, ~1,000 MW full build) as one of two co-equal power options (the other: BC Hydro grid); choice not finalized when cancelled. | up to ~500-1,000 MW (design option, not selected) | https://projects.eao.gov.bc.ca/api/document/5be33b1e578b640024f5d4ac/download
Pacific NorthWest LNG Terminal | T100000130363 | Canada | Cancelled - excluded per instruction. Federal EA Decision Statement condition 3.1.5 mandated aero-derivative gas turbines driving the refrigerant compressors (mechanical drive). No MW disclosed. | None disclosed (mechanical drive) | http://web.archive.org/web/20170802063139/http://www.pacificnorthwestlng.com/media/PNW_fsAirQuality_V3.pdf https://iaac-aeic.gc.ca/050/evaluations/document/115669
Prince Rupert LNG Terminal | T100000130364 | Canada | Cancelled - excluded per instruction. IAAC project description: gas-turbine mechanical-drive compression (~540 MW shaft class) plus separate on-site gas-turbine generation for plant electrical load (fully islanded design). | ~540 MW shaft class (design) | https://www.iaac-aeic.gc.ca/050/documents/p80042/88546E.pdf
Bahia Blanca GasPort FSRU | T100000130538 | Argentina | No MW figure disclosed (and idled). FSRU Excelerate Excelsior onboard dual-fuel engines burning predominantly LNG/BOG per Excelerate fleet-wide disclosure (FSRU-onboard convention). | None | https://excelerateenergy.com/our-operations/floating-lng-terminals/ https://excelerateenergy.com/wp-content/uploads/2025/08/Excelerate-Energy-2024-SR-080125.pdf
Escobar FSRU | T100000130542 | Argentina | No MW figure disclosed. FSRU Excelerate Expedient onboard dual-fuel engines burning predominantly LNG/BOG per Excelerate fleet-wide disclosure (FSRU-onboard convention). | None | https://excelerateenergy.com/our-operations/floating-lng-terminals/ https://excelerateenergy.com/wp-content/uploads/2025/08/Excelerate-Energy-2024-SR-080125.pdf
Bahia FSRU | T100000130925 | Brazil | No MW figure disclosed. FSRU Excelerate Sequoia onboard dual-fuel generating plant run predominantly on BOG per Excelerate fleet-wide disclosure (FSRU-onboard convention). | None | https://excelerateenergy.com/projects/bahia-brazil-tr-ba/ https://excelerateenergy.com/wp-content/uploads/2025/08/Excelerate-Energy-2024-SR-080125.pdf
Cosan FSRU | T100000130927 | Brazil | No MW figure disclosed. FSRU Hoegh Giant onboard generating plant, gas-capable per Hoegh Evi's fleet-wide disclosure (FSRU-onboard convention; fleet-wide claim, not vessel-specific spec). | None | https://hoeghevi.com/about/fleet/ https://hoeghevi.com/sustainability/environment/
Guanabara Bay FSRU | T100000130546 | Brazil | No MW figure disclosed. FSRU Excelerate Experience onboard dual-fuel generating plant run predominantly on BOG per Excelerate fleet-wide disclosure (FSRU-onboard convention). | None | https://excelerateenergy.com/projects/guanabara-bay-lng-import-terminal/ https://excelerateenergy.com/wp-content/uploads/2025/08/Excelerate-Energy-2024-SR-080125.pdf
New Fortress Barcarena FSRU | T100000130926 | Brazil | No MW figure disclosed. FSRU Energos Celsius runs Wartsila TFDE (tri-fuel diesel-electric) generator sets with a BOG recondenser per Energos Infrastructure's own fleet page (vessel-specific; FSRU-onboard convention). | None | https://energosinfra.com/fleet https://www.marinelink.com/news/new-fortress-energy-takes-delivery-510361 https://www.sec.gov/Archives/edgar/data/1749723/000174972324000011/nfe-20231231.htm
Sergipe FSRU | T100000130664 | Brazil | No MW figure disclosed. FSRU Energos Nanook fitted with Wartsila DFDE generation per the operator's fleet spec page (FSRU-onboard convention). Separate from the 1,500 MW Porto de Sergipe CCGT the terminal supplies (fuel-supply-OUT, not captive). | None | https://energosinfra.com/fleet-assets/
Cartagena FSRU (Colombia) | T100000130562 | Colombia | No MW figure disclosed. FSRU Hoegh Grace built with Wartsila-Hyundai DFDE generating engines (FSRU-onboard convention). | None | https://www.marineinsight.com/hoegh-lng-takes-delivery-of-ninth-fsru-hoegh-gannet/ https://www.offshore-energy.biz/hoegh-lng-names-6th-fsru-at-hhi/
Manzanillo (Dominican Republic) LNG Terminal | T100000131094 | Dominican Republic | No MW figure disclosed. FSRU Energos Freeze onboard steam-turbine plant with dedicated high-pressure BOG compressors (boilers fired on boil-off gas) per Energos Infrastructure's fleet page (vessel- and site-specific; FSRU-onboard convention). The 2x430 MW + 414 MW onshore plants it feeds are fuel-supply-OUT, not captive. | None (onboard); onshore customer plants are not captive | https://bankinformationcenter.org/project/manzanillo-gas-power-s-a/ https://energosinfra.com/fleet https://lngprime.com/americas/nfe-seals-dominican-fsru-charter-deal/150997/ https://www.newsfilecorp.com/release/292153/Energia-2000-Commissions-414-MW-Manzanillo-Power-Plant-in-Dominican-Republic
Old Harbour FSRU | T100000130684 | Jamaica | No MW figure disclosed. FSRU Hoegh Gallant, gas-capable per Hoegh Evi's fleet-wide disclosure (FSRU-onboard convention; fleet-wide claim). The three downstream customer plants (190 MW JPS Old Harbour etc.) are fuel-supply-OUT, not captive. | None | https://hoeghevi.com/about/fleet/ https://hoeghevi.com/sustainability/environment/ https://jpt.spe.org/excelerate-buys-new-fortress-jamaican-assets-for-1-billion https://lngprime.com/americas/hoegh-gallant-fsru-ready-to-start-jamaica-job/34879/
Sinolam LNG Terminal | T100000131082 | Panama | Shelved - excluded per instruction (also no MW disclosed). FSU GasLog Singapore (TFDE LNG carrier conversion): onboard tri-fuel diesel-electric gensets, gas-capable (FSU-onboard convention). The downstream Sinolam Smarter Energy plant is fuel-supply-OUT, not captive. | None | https://www.bairdmaritime.com/shipping/tankers/gas/gaslog-wins-10-year-charter-in-panama-for-lng-fsu